## Spare Parts Summary
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
DO NOT UPDATE/MODIFY INFORMATION IN THIS SHEET, DO IN INDIVIDUAL SECTION SHEETS - SHEET FILTERS FOR ALL ITEMS THAT HAVE SPARE PARTS
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | Comments | General Information | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Guide Vanes
Guide Vanes | Component | O-60620/O-60621 | N/A | Guide Vane Lever Lower Part | Premachined, lower part (thrust surface) of guide vane lever | 20 | 0 | New design from refurbishment | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-GVA | 6 | 0
Guide Vane Lever | Component | O-27672/O-60600 | N/A | Guide Vane Key | Gib Head Key - AS 3678-250 Plate | 20 | Will there be a new drawing for this? | Used to pin the Guide Vane to the Leaver, Not referenced on any drawing | Y | S&W | Matt | N/A | 0 | Tub 1 | WL-1-TUR-GVA | 5 | 0
Guide Vane Lever | Component | O-27672/O-60600 | N/A | Guide Vane Adjusting Liner | Adjusting Liner for setting Centre Height - AS 3678-250 | 20 | Will there be a new drawing for this? | Used to set the position within the Check Plates, Not referenced on any drawing | Y | S&W | Matt | N/A | 0 | Tub 1 | WL-1-TUR-GVA | 20 | 0
Guide Vane Link | Component | O-25959 | 7 | Shear Pin | New in equiv. to ASTM 1035 | 20 | Will there be a new drawing for this? | See drawing O-60610 for manufacturing details | Y | Voith | Matt | N/A | 0 | Tub 5 | WL-1-TUR-GVA | 23 (10 left at WL Site) | 0
Guide Vane Link | Bearing | O-25959 | 8 | Guide Vane Link Bush | DU Bearings Zinc Plated Backing | 40 | Will there be a new drawing for this? Are there spares? | For use with both the Link Pin and Shear Pin and is to be installed in the Guide Vane Link | Y | Voith | Matt | N/A | 0 | ? | WL-1-TUR-GVA | 10 | 0
Guide Vane Link | Component | O-25959 | 9 | Shear Pin Monitoring Device | Fixed Pin, Ø3 | 20 | 0 | O-27870 | Y | S&W | Matt | N/A | 0 | Tub 2 | WL-1-TUR-GVA | 32 | 0
Guide Vane Link | Component | O-25959 | 12 | Guide Vane Link Pin | Link Pin (fixed), Ø40 | 20 | Supplied new in SS | O-27866 Installed in the Regulating Ring, spares premachined | Y | Voith | Matt | N/A | 0 | Tub 5 | WL-1-TUR-GVA | 5 | 0
Upper Bearing Housing | Bearing | O-25959 / O-60600 | 5 | Lower Thurst Bearing Liner | Deva Tex | 20 | Will there be a new drawing for this? Are there spares? Supplied fit to housing and final machined to 0.03 flatness, 1.6 Ra | They are to be adhered to the Upper Bearing Housing - See O-60259 | Y | S&W | Matt | N/A | 0 | Installed in Upper Bearing Housing | WL-1-TUR-GVA | 5 | 0
Lower Bearing Housing | Seal | O-27672 / O-60600 | N/A | Lower Bearing Housing Top Outer Seal | P140 NBR70 O'Ring (139.6mm x 5.7mm) | 20 | Confirmed as-built | 0 | Y | Site | Tom | N | 0 | Tub 3 | WL-1-TUR-GVA | 2 | 0
Lower Bearing Housing | Seal | O-27672 / O-60600 | N/A | Lower Guide Vane Shaft Seal | P90 NBR70 O'Ring (89.6mm x 5.7mm) | 20 | Confirmed as-built | Fits into the Lower Cheek Plate | Y | Site | Tom | Y | Y | Tub 3 | WL-1-TUR-GVA | 4 | 0
Lower Bearing Housing | Component | O-27672 / O-60600 | N/A | Lower Guide Vane Bearing Housing | Lower Bearing Housing | 20 | New | See O-60590 for detailed drawing | Y | S&W | Matt | N/A | 0 | S&W | WL-1-TUR-GVA | 1 | 0
Lower Bearing Housing | Bearing | O-27672 / O-60600 | N/A | Lower Bearing Housing Bush | IDØ89 Deva.Tex | 20 | Will there be a new drawing for this? Are there spares? | No details listed on drawing | Y | S&W | Matt | N/A | 0 | Installed in Lower Bearing Housing | WL-1-TUR-GVA | 5 | 0
Upper Bearing Housing | Component | O-27672 / O-60600 | N/A | Upper Bearing Housing | Upper Bearing Housing | 80 | New | See O-60613 for detailed drawing | Y | S&W | Matt | N/A | 0 | S@W | WL-1-TUR-GVA | 1 | 0
Upper Bearing Housing | Bearing | O-27672 / O-60600 | N/A | Upper Bearing Housing Bush | IDØ99 Deva.Tex | 40 | Will there be a new drawing for this? Are there spares? | Two bushes per Bearing Housing | Y | Voith | Matt | N/A | 0 | Installed in Upper Bearing Housing | WL-1-TUR-GVA | 10 | 0
Upper Bearing Housing | Bearing | O-25959 | 4 | Upper Thurst Bearing Liner | Deva.Tex | 20 | 0 | O-60260 There are 2 halves to each Carbon Ring set and they are to be adhered to the Upper Thurst Bearing Holder | Y | S&W | Matt | Y | 0 | Installed in Thrust Bearing Holder Rings | WL-1-TUR-GVA | 4.5 | 0
Upper Bearing Housing | Seal | O-27672/O-60600 | H514332 | Upper Bearing Housing Inner Seal | Hydraulic Rod Seal - PU, 99IDx130ODx15 | 20 | 0 | No details listed on drawing | Y | Site | Tom | N | 0 | Tub 4 | WL-1-TUR-GVA | 4 | 0
Upper Bearing Housing | Fastener | O-27672/O-60600 | H502353 | Upper Bearing Housing Inner Seal Retainer | Circlip (Retaining Ring, d1=135 acc. To DIN 472) | 20 | 0 | No details listed on drawing | Y | S&W | Matt | N/A | 0 | Tub 4 | WL-1-TUR-GVA | 30 | 0
Upper Bearing Housing | Component | O-27672/O-60600 | H534652 | Upper Bearing Housing Inner Seal Energiser | Steel Ring Energiser (Packing Support) | 20 | 0 | No details listed on drawing | Y | S&W | Matt | N/A | 0 | Tub 4 | WL-1-TUR-GVA | 5 | 0
Upper Bearing Housing | Component | O-27672/O-60600 | H534651 | Upper Bearing Housing Inner Seal Packing Support | Steel Ring (Packing Support) 130OD x 6thk | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-GVA | 6 | 0
Bottom Ring
Bottom Ring | Fastener | O-27715 | 15 | Stud for Bottom Ring | M38 x 2mm Pitch, plain steel, 4140 | 32 | Supplied new from Voith | 0 | Y | Voith | Tom | Y | Y | Installed | WL-1-TUR-COV | 8 | 0
Bottom Ring | Fastener | O-27715 | 16 | Nut | M38 x 2mm Pitch, plain steel, 4140 | 32 | New ones made to suit Voith Studs | 0 | N | Site | Tom | Y | Y | Installed | WL-1-TUR-COV | 9 | 0
Bottom Ring | Fastener | 0 | N/A | Nut Cover | Nylon nut cover | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-COV | 5 | 0
Top Cover
Top cover | Fastener | O-27712 | 27 | Stud | M38 x 2mm Pitch, plain steel, 4140 | 32 | Supplied new from Voith | 0 | Y | Voith | Matt | Y | Y | Installed | WL-1-TUR-COV | 8 | 0
Top cover | Fastener | O-27712 | 28 | Nut | M38 x 2mm Pitch, plain steel, 4140 | 32 | New ones made to suit Voith Studs | 0 | Y | Site | Tom | Y | Y | Installed | WL-1-TUR-COV | 9 | 0
Top Cover | Fastener | 0 | N/A | Nut Cover | Nylon nut cover | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-COV | 5 | 0
Upper Guide & Thrust Bearing
Bearing shell | Seal | O-27136-003 | 21 | Rubber for Sealing Bearing Segments | 12 x 65, 95 nitr | 12 | 0 | 2 pieces between each segment, glued in place | N | Cambridge | Matt | N | N | Tub 1 | WL-1-ALT-THG-GB1 | 9 | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 3 | Upper spring plate | 0 | 0 | 0 | These spares are at Cambridge? | N/A | 0 | 0 | 0 | 0 | N/A | WL-1-ALT-THG-THR | 12 TBC (Cambridge) | Already in System?
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 4 | Lower spring plate | 0 | 0 | 0 | These spares are at Cambridge? | N/A | 0 | 0 | 0 | 0 | N/A | WL-1-ALT-THG-THR | 12 TBC (Cambridge) | Already in System?
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 5 | Thrust pads | 0 | 0 | 0 | item 2 on drawing O-26349 | N/A | 0 | 0 | 0 | 0 | N/A | WL-1-ALT-THG-THR | 12 TBC (Cambridge) | Already in System?
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 6 | Upper Guide Bearing shell | 0 | 0 | 0 | Type 2 on drawing O-27136 | N/A | 0 | 0 | 0 | 0 | N/A | WL-1-ALT-THG-GB1 | 1 (Cambridge) | Already in System?
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 7 | Thrust block & runner | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | N/A | WL-1-ALT-THG | 1(Cambridge) | 0
Upper Spring Plate | Component | O-27490 | 6 | Ring for Upper Spring Plate | Support Ring for Upper Spring Plate | 12 | 0 | Used to secure the Upper Spring Plate to the Thrust Pad | Y | Cambridge | Matt | N/A | Y | Tub 2 | WL-1-ALT-THG-THR | 12 | Already in System?
Thrust Bracket
Thrust Bracket | Component | O-59796-001 | 1 | Shim for Thrust Bracket | Various Thickness' | 1 | For shimming the Thrust Bracket to correct level | 0 | Y | Andritz | Tom | N/A | Y | Inward Goods Store | WL-1-ALT-THG | 1 | 0
Thrust Block
C-Keys | Component | O-27089 | 5 | Thrust Ring | Splits in two, known as C-Keys | 1 | 0 | 0 | Y | Cambridge | Matt | N/A | Y | Loading Bay | WL-1-ALT-THG | 1 (Cambridge) | 0
C-Keys | Component | O-27089 | 6 | Lock Ring for Thrust Ring | Keeper for the C-Keys | 1 | 0 | 0 | Y | Cambridge | Matt | N/A | Y | Operating Floor | WL-1-ALT-THG | 1 (Cambridge) | 0
Lower Guide Bearing
LGB | Component | O-26341 | 1 | Bearing Half | US Half? | 1 | 0 | 0 | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-GB1 | 1 | 0
LGB | Component | O-26341 | 2 | Bearing Half | LB Half? | 1 | 0 | 0 | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-GB1 | 1 | 0
Brakes & Jacks
Lower Bracket
Lower Bracket | Component | O-27609-002 | 2 | Lower Bracket Shim - 1mm | 1mm Shim plate, plain steel | 8 | For setting of Lower Bracket RL and Level | 0 | Y | Site | Tom | Y | 0 | Inward Goods Store | WL-1-ALT-GB1 | TBC | 0
Lower Bracket | Component | O-27609-002 | 3 | Lower Bracket Shim - 1mm | 2mm Shim plate, plain steel | 8 | For setting of Lower Bracket RL and Level | 0 | Y | Site | Tom | Y | 0 | Inward Goods Store | WL-1-ALT-GB1 | TBC | 0
Lower Bracket | Component | O-27609-002 | 4 | Lower Bracket Shim - 1mm | 3mm Shim plate, plain steel | 4 | For setting of Lower Bracket RL and Level | 0 | Y | Site | Tom | Y | 0 | Inward Goods Store | WL-1-ALT-GB1 | TBC | 0
Runner and Turbine Shaft
Runner | Component | O-27256 | 2 | Wearing ring | Wearing ring O-60616 | 1 | The runner wearing ring wasn’t replaced so should be a spare?? | 0 | Y | 0 | 0 | 0 | 0 | N/A | WL-1-TUR-RUN | 1 | 0
Spiral Casing
Upper & Lower Fan Rings
Draft Tube
Turbine Guide Bearing
Turbine Guide Bearing | Component | O-27717 Rev:B | 1 | ? | 0 | 2 | 0 | Need to get Mandy to lighten draing so we can see it better | 0 | 0 | 0 | 0 | 0 | N/A | WL-1-TUR-GB1 | 2? | 0
Oil Level Device | Component | A2-07831-020 | 59 | Oil Level Sight Glass | Oil Level Sight Glass - Alemlube FGB2200 | 1 | Spare is for glass tube only | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-GB1 | 1 | 0
TGB Cooler | Component | O-26404 | 1 | Cooler Calibration Tube | Cooler Calibration Tube 11ODx1Thk 90/10 CuNi | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-GB1-HTX | 1 | 0
Brushgear
Shaft Seal
Carbon Ring Holder | Component | O-25849 | 47 | Carbon Rings | Carbon | 2 | Glued in Item 48 | 0 | Y | 0 | 0 | 0 | 0 | Installed | WL-1-TUR-SHT-SEA | TBC | 0
Carbon Ring Holder | Component | O-27673 | 16 | Springs for Carbon Ring Holder | O-60305 | 16 | 0 | Confirm Details? | Y | 0 | 0 | 0 | 0 | Tub 3 | WL-1-TUR-SHT-SEA | 16 | 0
Carbon Ring Holder | Component | O-25849 | N/A | Glue for Carbon Rings | Araldite Huntsman 2014-2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-SHT-SEA | 1 | 0
Other Components
Cooling Water Pump | Component | O-60741-002 | 4 | Motor Stool Seal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Component | O-60741-002 | 5 | Motor Stool Bearing | NSK 6307C3 or NSK 6307VVC3E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Seal | O-60741-002 | 6 | Motor Stool Bearing O-Ring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 2 | 0
Cooling Water Pump | Component | O-60741-002 | 10 | Intermediate Bearing Bush | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Seal | O-60741-002 | 12 | Intermediate Bearing O-Ring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Component | O-60741-002 | 14 | Bottom Bearing | NSK 6307C3 or NSK 6307VVC3E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Seal | O-60741-002 | 16 | Secondary Mechanical Seal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Seal | O-60741-002 | 18 | Primary Seal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Component | O-60741-002 | 20 | Impeller Key | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Component | O-60741-002 | 21 | Impeller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Component | O-60741-002 | 22 | Impeller Nut | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Seal | O-60741-002 | 24 | Casing O-Ring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | TBC | 0
Cooling Water Pump | Component | O-60741-002 | 25 | Casing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1 | 0
Cooling Water Pump | Seal | O-60741-002 | 31 | Bottom Bearing O-Ring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-CWS-PS1, WL-1-CWS-PS2 | 2 | 0
Regulating Ring | Component | O-60601 | N/A | Axial Bearing Strip | Regulating Ring Axial Bearing Strip, DU Bearing 160x30x3 | 18 | Supplied with mandrel punch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-RGS | 18 | 0
Regulating Ring | Component | O-60594 | N/A | Radial Bearing Strip | Regulating Ring Radial Bearing Strip, DU Bearing 500x70x3 | 6 | Supplied with mandrel punch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-RGS | 6 | 0
Regulating Ring | Component | O-28157 | 14 | Regulating Mechanism Thrust Liner | O-28160 Regulating Mechanism Thrust Liner - DU Dry Bearing (two halves) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-RGS | 1 | 0
Generator Pit Cover | Seal | O-26996 | 15 | Floor Plate Seal | Seal inbetween 4 floor plates | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT | ~10m | 0
Generator Pit Cover | Seal | O-26996 | 16 | Floor Plate Seal | Seal inbetween inside diameter of floor plates and thrust bracket oil pot | 10m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT | ~10m | 0
Guide Vane Servomotor | Seal | O-25570 | 22 | Rod Seal | SKF Rod Seal ID135 OD165 H16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-RGS-ACT | 1 | 0
Guide Vane Servomotor | Seal | O-25570 | 25 | O-Ring Vulcanised | O-Ring Vulcanised 410x7 - Endcaps to body | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-TUR-RGS-ACT | 2 | 0
Distributing Valve | Seal | A1-16120 | 29 | O-Ring P16 | O-Ring P16 Duro 70 (15.8 x 2.4) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-GOV-CTE | 2 | 0
Distributing Valve | Seal | A1-16120 | 44 | O-Ring G150 | O-Ring G150 Duro 70 (149.3x5.7) | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-GOV-CTE | 6 | 0
Distributing Valve | Seal | A1-16120 | 43 | O-Ring P110 | O-Ring P110 Duro 70 (109.6x5.7) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-GOV-CTE | 1 | 0
Alternator Water Spray | Components | N/A | N/A | Fittings Misc | AWS Fittings Misc | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-FDS | 1 | 0
Alternator Water Spray | Components | N/A | N/A | Hose | AWS Hose | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-FDS | 1 | 0
Governor Hydraulic | Components | O-60737 | N/A | Governor Accumulator PRV | Set to 2440kPa | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-GOV-HYD-PV1-SV1 | 1 | 0
Governor Air Compressor | Components | O-60624 | 0 | Air Filter Element | Ingersol Rand part no 32170979 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-S-CAS-CP1 | 1 | 0
Main Inlet Valve
MIV Bypass Valve | Seal | O-60584-002 | 83.02 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=183.52 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.03 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=142.24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 2 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.07.01 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=59.69 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.07.02 | Guide Ring | Guide Ring PTFE + Bronze, Ø40 x Ø43 x 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.07.03 | Groove Ring | Groove Ring Polyurethane Ø40 x Ø60 BL=11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.08.01 | Groove Ring | Groove Ring Polyurethane Ø40 x Ø60 BL=11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.08.02 | Guide Ring | Guide Ring PTFE + Bronze, Ø40 x Ø43 x 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.08.03 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=100.97 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 2 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.08.04 | Groove Ring | Groove Ring Polyurethane Ø40 x Ø60 BL=11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 2 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.08.05 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=148.59 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 2 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.08.06 | Groove Ring | Groove Ring Polyurethane Ø20 x Ø30 BL=6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 2 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.08.07 | Guide Ring | Guide Ring PTFE + Bronze, Ø20 x Ø23 x 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.08.08 | Wiper Seal | Wiper Polyurethane Ø20 x Ø28 #4/7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.10.1 | Piston Seal | Piston Seal NBR + POM + Polyester Ø160 x Ø130 x 25.4/12.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.10.2 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=37.47 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-BV1 | 1 (TBC) | 0
MIV Servomotor | Component | A1-16274 | 0 | Flexible Hose Ferrule | Ferrule, SS Pegasus Hydraulics P/N P1-DN 31 | 8 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 8 | 0
MIV Servomotor | Component | A1-16274 | 0 | Flexible Hose Hose Tail 90 Degree | SAE Code 61 Flanged Insert 90 Degree, SS, Pegasus Hydraulics P/N SFL3-1 1/4"-DN 31 | 8 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 4 On order | 0
MIV Servomotor | Component | A1-16274 | 0 | Flexible Hose Hose Tail | SAE Code 61 Flanged Insert, SS, Pegasus Hydraulics P/N SFL3-1 1/4"-DN 31 | 8 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 4 | 0
MIV Servomotor | Component | O-60687-001 | 4066464 | Clevis Bush | CuSn7Zn4Pb7 Bush | 4 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
MIV Servomotor | Component | O-60687-001 | 4066466 | Clevis Adjustment Ring | Clevis Adjustment Ring, Stainless Steel 17-4 PH | 2 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
MIV Servomotor | Component | O-60687-001 | 4066585 | Anti-slam orifice blank | M30x2 SS Blank Orifice | 2 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
MIV Servomotor | Seal | O-60687-001 | 01 | Rod Seal | Rod Seal ø480 (OD) | 4 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
MIV Servomotor | Bearing | O-60687-001 | 02 | Guide Ring | Guide Ring - Hallite Type 506, 25 x 4 x Ø485OD | 4 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
MIV Servomotor | Seal | O-60687-001 | 03 | Rod Seal | Rod Seal, Two Piece, Ø115ID | 2 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 1 | 0
MIV Servomotor | Seal | O-60687-001 | 04 | Lip Seal | Lip Seal, Ø115ID | 2 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 1 | 0
MIV Servomotor | Bearing | O-60687-001 | 05 | Guide Ring | Guide Ring - Hallite Type 506, 25 x 4 x Ø115OD | 2 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 1 | 0
MIV Servomotor | Seal | O-60687-001 | 06 | O-Ring | O-Ring | 4 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
MIV Servomotor | Seal | O-60687-001 | 07 | O-Ring | O-Ring, Ø485ID | 2 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
MIV Servomotor | Seal | O-60687-001 | 08 | O-Ring | O-Ring, Ø5.33x115ID | 4 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
MIV Servomotor | Seal | O-60687-001 | 08 | O-Ring | O-Ring, Ø5.33x115ID | 2 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
MIV Servomotor | Component | O-60687-002 | 4066470 | Stroke Adjustment Ring | Stroke Adjustment Ring, Stainless Steel AISI 316L | 2 | 0 | Qty total for both servomotors | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-MIV-ACT | 2 | 0
Relief Valve
Rotor
Rotor Assembly | Component | O-27636 | 8 | Rotor Pole Complete | Detailed Drawing O-59714 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-ROT-POL | 1 | 0
Rotor Pole Fixing | Component | O-59717 | 1 | Slide Wedge right | O-59928 (300889892) Pos 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-ROT-POL | 2 (TBC) | 0
Rotor Pole Fixing | Component | O-59717 | 2 | Slide Wedge left | O-59928 (300889892) Pos 2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-ROT-POL | 2 (TBC) | 0
Rotor Pole Fixing | Component | O-59717 | 3 | Body Wedge right | O-59928 (300889892) Pos 3 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-ROT-POL | 2 (TBC) | 0
Rotor Pole Fixing | Component | O-59717 | 4 | Body Wedge left | O-59928 (300889892) Pos 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-ROT-POL | 2 (TBC) | 0
Rotor Pole Fixing | Component | O-59717 | 12 | Compensating sheet for pole fixing (Shim) | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-ROT-POL | TBC | 0
Stator
Stator Core | Fastener | O-59723 | 7 | Stator Pressing Bolt | Bolt M20x1, 5x1158 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-COR | 1 (TBC) | 0
Stator Winding | Component | O-59722 | 2 | Roebel Bar Bent (Top Bar) | Part drawing O-59916 (300865129) | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 16 (TBC) | 0
Stator Winding | Component | O-59722 | 3 | Roebel Bar Bent (Bottom Bar) | Part drawing O-60191 (300865137) | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 2 (TBC) | 0
Stator Winding | Component | O-59722 | 4 | Roebel Bar Bent (Connection Bar) | Part drawing O-60184 (30086540) | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 4 (TBC) | 0
Stator Winding | Component | O-59722 | 5 | Seperator | 6x21x990 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 20 (TBC) | 0
Stator Winding | Component | O-59722 | 6 | Insulating Cap | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 40 (TBC) | 0
Stator Winding | Component | O-59722 | 13 | Stator Winding Connection Copper Parts Insulated | FLAT BAR 50 X 8 X 130 | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 160 (TBC) | 0
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 9 x 30 x 47 EPGC 203 - EN 60893 | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 40 (TBC) | 0
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 2 x 30 x 47 EPGC 203 - EN 60893 | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 40 (TBC) | 0
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 1 x 30 x 47 EPGC 203 - EN 60893 | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 40 (TBC) | 0
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 9 x 30 x 44 EPGC 203 - EN 60893 | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 200 (TBC) | 0
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 2 x 30 x 44 EPGC 203 - EN 60893 | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 200 (TBC) | 0
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 1 x 30 x 44 EPGC 203 - EN 60893 | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | WL-1-ALT-STR-WDG | 200 (TBC) | 0
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 42mm | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 (TBC) | 0
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 47mm | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 (TBC) | 0
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 52mm | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 (TBC) | 0
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 37mm | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 (TBC) | 0
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 37mm | ? | 0 | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 (TBC) | 0
Instrumentation
Dewatering pump control | PLC | F-01820-005-002/003 | 34DW | Dewatering PLC | 1766-L32BXB | 1 | [8 empty] | WL-S-DW1 | TBC | 0
Dewatering pump control | float switch | GEN-0141-00002-001 | LS5000 - LS5006 | Dewatering Pit Floats | ENM-10 float switch | 6 | [8 empty] | WL-S-DW1 | TBC | 102761
Alternator | Flow sensor | O-60024-UCB4-62, A1-15261-602 | FIT2021 | ALTERNATOR BEARING OIL COOLERS RETURN FLOW SENSOR | SA4100 PLUS EVC 561 CABLE (30m), E40258 Progressive Ring Fitting (G1/2 Compression Fitting) | 1 | [8 empty] | WL-1-ALT-THG-HTX | TBC | 0
Alternator | Flow sensor | O-60024-UCB4-62, A1-15261-510 | FIT2133 | TURBINE BEARING OIL COOLERS RETURN FLOW SENSOR | SA4100 PLUS EVC 561 CABLE (30m), E40267 Progressive Ring Fitting (G1/2 Compression Fitting) | 1 | [8 empty] | WL-1-TUR-GB1-HTX | TBC | 0
Alternator | Flow meter | O-60024-UCB4-50, A1-15261-425 | FIT3012 | ALTERNATOR AIR COOLERS RETURN FLOW METER | AFX125G-NNAH1S-AA11-4NB 125mm | 1 | [8 empty] | WL-1-CWS-FLR | TBC | 0
Switch Yard | Flow meter | O-60024-UCB4-51, A1-15261-426 | FIT3025 | TRANSFORMER SUPPLY FLOW METER | AFX080G-NNAH1S-AA11-4NB 80mm | 1 | [8 empty] | WL-1-CWS-FLR | TBC | 300987
Alternator floor | Flow meter | O-60024-UCB4-50, A1-15261-425 | FIT3072 | ALTERNATOR LOWER GUIDE BEARING WATER FLOW RELAY | AFX040G-NNAH1S-AA11-4NB 40mm | 1 | [8 empty] | WL-1-CWS-FLR | TBC | 303621
Turbine pit | Flow meter | O-60024-UCB4-51, A1-15261-425 | FIT3082 | TURBINE SEAL WATER SUPPLY FLOW METER | AFX025G-NNAH1S-AA11-4NB 25mm | 1 | [8 empty] | WL-1-CWS-FLR | TBC | 301196
Turbine Pit | Flow meter | O-60024-UCB4-50, A1-15261-425 | FIT3095 | TURBINE GUIDE BEARING OIL COOLER RETURN WATER FLOW METER | AFX040G-NNAH1S-AA11-4NB 40mm | 1 | [8 empty] | WL-1-CWS-FLR | TBC | 303621
Alternator floor | Flow meter | O-60024-UCB4-50, A1-15261-425 | FIT3098 | ALTERNATOR UPPER GUIDE BEARING OIL COOLERS RETURN FLOW METER | AFX080G-NNAH1S-AA11-4NB 80mm | 1 | [8 empty] | WL-1-CWS-FLR | TBC | 300987
HTVH | PLC | F-01820-015-002/004 | 34HH | HTV PLC | 1769-L33ER | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 161761???
HTVH | PLC IO card | F-01820-015-002/004 | 34HH | HTV PLC IO cards | 1769-IF8 | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 162237
HTVH | PLC IO card | F-01820-015-002/004 | 34HH | HTV PLC IO cards | 1769-IQ16 | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 162211
HTVH | PLC IO card | F-01820-015-002/004 | 34HH | HTV PLC IO cards | 1769-OB16 | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 161779
HTVH | PLC IO card | F-01820-015-002/004 | 34HH | HTV PLC IO cards | 1769-PB4 | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 162245
HTVH | PLC screen | F-01820-015-001/004 | 34HH-PV | HTV Panel View | 2711P-B7C4D8 | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 0
HTVH | Posistion Transducer | F-01759-015-023 | 99HV1 | HTV Position Transducer | KINAX N702 | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 0
IG | level transducers | A2-07831-700 A3-15261-H285 | LT7000, LT7002, LT7003 | Level Transducers (lake, tunnel, trachrack) | FMP51-AAACCBLAA4GDJ-LAOC with 21m Rope | 3 | [8 empty] | WL-1-NT1-GT1-CTE | TBC | 0
IG | Pressure Transducer | A3-15261-H285 | PT9001 | Intake Cylinder Oil Pressure | PN3092 PLUS EVC 561 CABLE (30m) | 1 | [8 empty] | WL-1-NT1-GT1-CTE | TBC | 302695 300963(cable)
IG | Pressure Transducer | A3-15261-H285 | PT9002 | Intake Pilot Line Oil Pressure | PN3092 PLUS EVC 561 CABLE (30m) | 1 | [8 empty] | WL-1-NT1-GT1-CTE | TBC | 302695 300963(cable)
IG | Position indicator | A-16338 | ZT9000 | Intake Gate Position | RP-S-0900M-D60-1-A01 plus accessories as per drawing +plug | 1 | [8 empty] | WL-1-NT1-GT1-CTE | TBC | 0
Turbine | Level Indicator | A2-07831-020 | LI0038 | OIL LEVEL INDICATOR | FGB2250 Turbine bearing OIL LEVEL SIGHT GUAGE | 1 | [8 empty] | WL-1-TUR-GB1 | TBC | 0
Governor | Level Switch | A2-07831-100 | LS1570 | GOVERNOR SUMP TANK OIL LEVEL SWITCH | LSP-1-800-8-1BSP C/F-A | 1 | [8 empty] | WL-1-GOV-HYD | TBC | 0
Turbine | Level Transmitter | O-60024-UCB3-34, A1-15261-510 | LT0036 | OIL LEVEL TRANSMITTER FOR TURBINE GUIDE BEARING OIL RESERVOIR | RHH0390MD601A01, COMPLETE WITH FLOAT PART No. 251447 & COLLAR PART No. 56077 + Plug | 1 | [8 empty] | WL-1-TUR-GB1 | TBC | 0
Alt Upper Guide | Level Transmitter | A2-07831-070 | LT0500 | ALTERNATOR UPPER GUIDE & THRUST BEARING OIL LEVEL TRANSMITTER | RHM0240MD601A01, COMPLETE WITH FLOAT PART No. 251447 & COLLAR PART No. 56077 + Plug | 1 | [8 empty] | WL-1-ALT-THG | TBC | 0
Alt Lower Guide | Level Transmitter | A2-07831-060 | LT0554 | ALTERNATOR LOWER GUIDE BEARING OIL LEVEL TRANSMITTER | RHM0240MD601A01, COMPLETE WITH FLOAT PART No. 251447 & COLLAR PART No. 56077 + Plug | 1 | [8 empty] | WL-1-ALT-GB1 | TBC | 0
Governor | Level Transmitter | A2-07831-100 | LT1522 | GOVERNOR OIL PRESSURE TANK OIL LEVEL TRANSMITTER | LPR1B1B11A0XFICM01250S, COMPLETE WITH FLOAT PART No. 251981-2 | 1 | [8 empty] | WL-1-GOV-HYD-PV1 | TBC | 0
Cooling water | Pressure differential | O-60024-UCB4-53 | PDT3004 | COOLING WATER SUPPLY DUPLEX FILTER DIFFERENTIAL PRESSURE TRANSDUCER | 38TUPMD55-AA21BA67LGCHAJA1F Including wall mount bracket for sensor: 71101934 | 1 | [8 empty] | WL-1-CWS-FLR | TBC | 0
Control water | Pressure differential | O-60024-UCB4-53 | PDT3004 | CONTROL WATER DUPLEX FILTER DIFFERENTIAL PRESSURE TRANSDUCER | UPMD55-AA21BA67LGCHAJA1F Including wall mount bracket for sensor: 71101934 | 1 | [8 empty] | WL-1-MCW-FLT | TBC | 0
turbine | Pressure Transmitter | O-60024-UCB4-61, A1-15261-510 | PT3314 | TURBINE SHAFT SEAL COOLING WATER PRESSURE | PN3094 PLUS EVC 561 CABLE (30m) | 1 | [8 empty] | WL-1-CWS | TBC | 0
Turbine BRG | RTD | A2-07831-002 | TE0028 | TGB PAD RTD | PT100, DUPLEX RTD's | 1 | [8 empty] | WL-1-TUR-GB1 | TBC | 0
Turbine BRG | RTD | A2-07831-002 | TE0029 | TGB PAD RTD | PT100, DUPLEX RTD's | 1 | [8 empty] | WL-1-TUR-GB1 | TBC | 0
Turbine BRG | RTD | A2-07831-002 | TE0035 | TGB SUMP RTD | PT100, DUPLEX RTD's | 1 | [8 empty] | WL-1-TUR-GB1 | TBC | 0
Turbine BRG | RTD | A2-07831-002 | TE0070 | TGB PAD RTD | PT100, DUPLEX RTD's | 1 | [8 empty] | WL-1-TUR-GB1 | TBC | 0
Alternator Thrust Brg | RTD | A2-07831-002 | TE0501 | ALTERNATOR UPPER THRUST BEARING PAD TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-THR | TBC | 0
Alternator Thrust Brg | RTD | A2-07831-002 | TE0502 | ALTERNATOR UPPER THRUST BEARING PAD TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-THR | TBC | 0
Alternator Thrust Brg | RTD | A2-07831-002 | TE0503 | ALTERNATOR UPPER THRUST BEARING PAD TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-THR | TBC | 0
Alternator Thrust Brg | RTD | A2-07831-002 | TE0504 | ALTERNATOR UPPER THRUST BEARING PAD TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-THR | TBC | 0
Alternator upper guide brg | RTD | A2-07831-002 | TE0506 | THERMOMETER FOR BEARING SHELL | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-GB1 | TBC | 0
Alternator upper guide brg | RTD | A2-07831-002 | TE507 | THERMOMETER FOR BEARING SHELL | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-GB1 | TBC | 0
Alternator upper guide brg | RTD | A2-07831-002 | TE0509 | THERMOMETER FOR BEARING SHELL | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-GB1 | TBC | 0
Alternator upper guide brg | RTD | A2-07831-002 | TE0510 | THERMOMETER FOR BEARING SHELL | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-GB1 | TBC | 0
Alternator Lower guide brg | RTD | A2-07831-002 | TE0550 | ALTERNATOR LOWER GUIDE BEARING RTD | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-GB1 | TBC | 0
Alternator Lower guide brg | RTD | A2-07831-002 | TE0551 | ALTERNATOR LOWER GUIDE BEARING RTD | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-GB1 | TBC | 0
Alternator Lower guide brg | RTD | A2-07831-002 | TE0552 | ALTERNATOR LOWER GUIDE BEARING RTD | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-GB1 | TBC | 0
Alternator Lower guide brg | RTD | A2-07831-002 | TE0556 | ALTERNATOR LOWER GUIDE BEARING OIL RTD | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-GB1 | TBC | 0
Alternator Bearing Cooler | RTD | A2-07831-002 | TE2018 | ALTERNATOR BEARING OIL COOLERS SUPPLY TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-HTX | TBC | 0
Alternator Bearing Cooler | RTD | A2-07831-002 | TE2019 | ALTERNATOR BEARING OIL COOLERS RETURN TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-HTX | TBC | 0
Alternator Bearing Cooler | RTD | A2-07831-002 | TE2020 | ALTERNATOR BEARING OIL COOLERS RETURN TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-ALT-THG-HTX | TBC | 0
cooling water | RTD | A2-07831-002 | TE3002 | COOLING WATER SUPPLY TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-CWS | TBC | 0
Alternator Coolers | RTD | A2-07831-002 | TE3011 | ALTERNATOR AIR COOLERS RETURN TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-CWS | TBC | 0
Transformer coolers | RTD | A2-07831-002 | TE3019 | TRANSFORMER SUPPLY TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-CWS | TBC | 0
Transformer coolers | RTD | A2-07831-002 | TE3020 | TRANSFORMER SUPPLY TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-CWS | TBC | 0
Alternator Lower guide brg | RTD | A2-07831-002 | TE3071 | ALTERNATOR LOWER GUIDE BEARING RETURN WATER TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-CWS | TBC | 0
Turbine BRG | RTD | A2-07831-002 | TE3084 | TURBINE GUIDE BEARING OIL COOLER RETURN WATER TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-CWS | TBC | 0
Alternator Bearing Cooler | RTD | A2-07831-002 | TE3097 | ALTERNATOR BEARING OIL COOLERS RETURN TEMPERATURE | PT100, DUPLEX RTD's (0-100deg C) | 1 | [8 empty] | WL-1-CWS | TBC | 0
Intake | RTD | C-08667 | TE9020 | Intake Gate Sump RTD | PT100, DUPLEX RTD's | 1 | [8 empty] | WL-1-NT1-GT1-CTE | TBC | 0
Turbine | Vibration Accelerometer | A2-07831-010 | VE0025 | TOP COVER VIBRATION | 2 pin MIL-C-5015 wireable socket to match, low freq. industrical ceramic shear ICP accelerometer 500mV/g | 1 | [8 empty] | WL-1-TUR-GB1 | TBC | 401538
Turbine | Vibration Accelerometer | A2-07831-020 | VE0033 | TGB VIBRATION | 0 | 1 | [8 empty] | WL-1-TUR-GB1 | TBC | 401538
Turbine | Vibration Accelerometer | A2-07831-020 | VE0034 | TGB VIBRATION | 0 | 1 | [8 empty] | WL-1-TUR-GB1 | TBC | 401538
Alternator Lower guide brg | Vibration Accelerometer | A2-07831-060 | VE0078 | ALTERNATOR LOWER GUIDE BEARING VIBRATION | 0 | 1 | [8 empty] | WL-1-ALT-GB1 | TBC | 401538
Alternator Lower guide brg | Vibration Accelerometer | A2-07831-060 | VE0079 | ALTERNATOR LOWER GUIDE BEARING VIBRATION | 0 | 1 | [8 empty] | WL-1-ALT-GB1 | TBC | 401538
Alternator upper guide/Thust brg | Vibration Accelerometer | A2-07831-070 | VE0088 | ALTERNATOR UPPER GUIDE & THRUST BEARING VIBRATION | 0 | 1 | [8 empty] | WL-1-ALT-THG | TBC | 401538
Alternator upper guide/Thust brg | Vibration Accelerometer | A2-07831-070 | VE0089 | ALTERNATOR UPPER GUIDE & THRUST BEARING VIBRATION | 0 | 1 | [8 empty] | WL-1-ALT-THG | TBC | 401538
Alternator upper guide/Thust brg | Vibration Accelerometer | A2-07831-070 | VE0090 | ALTERNATOR UPPER GUIDE & THRUST BEARING VIBRATION | 0 | 1 | [8 empty] | WL-1-ALT-THG | TBC | 401538
Turbine Shaft | Speed Sensor | A2-07831-020/30 | ZS0006 | POLE BAND SPEED SENSOR | 374Z-03870 | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301815
Turbine Shaft | Speed Sensor | A2-07831-020/30 | ZS0007 | POLE BAND SPEED SENSOR | 374Z-03870 | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301815
Turbine Shaft | Speed Sensor | A2-07831-020/30 | ZS0008 | POLE BAND SPEED SENSOR | 374Z-03870 | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301815
Turbine Shaft | Speed Sensor | A2-07831-020/30 | ZS0009 | POLE BAND SPEED SENSOR | 374Z-03870 | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301815
Turbine Shaft | Speed Sensor | A2-07831-020/30 | ZS0010 | POLE BAND SPEED SENSOR | 374Z-03870 | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301815
Turbine | Limit Switch | A1-15261-650 | ZS0046 | REGULATING RING SHEAR PIN SENSOR No.1 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0047 | REGULATING RING SHEAR PIN SENSOR No.2 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0048 | REGULATING RING SHEAR PIN SENSOR No.3 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0049 | REGULATING RING SHEAR PIN SENSOR No.4 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0050 | REGULATING RING SHEAR PIN SENSOR No.5 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0051 | REGULATING RING SHEAR PIN SENSOR No.6 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0052 | REGULATING RING SHEAR PIN SENSOR No.7 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0053 | REGULATING RING SHEAR PIN SENSOR No.8 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0054 | REGULATING RING SHEAR PIN SENSOR No.9 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0055 | REGULATING RING SHEAR PIN SENSOR No.10 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0056 | REGULATING RING SHEAR PIN SENSOR No.11 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0057 | REGULATING RING SHEAR PIN SENSOR No.12 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0058 | REGULATING RING SHEAR PIN SENSOR No.13 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0059 | REGULATING RING SHEAR PIN SENSOR No.14 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0060 | REGULATING RING SHEAR PIN SENSOR No.15 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0061 | REGULATING RING SHEAR PIN SENSOR No.16 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0062 | REGULATING RING SHEAR PIN SENSOR No.17 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0063 | REGULATING RING SHEAR PIN SENSOR No.18 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0064 | REGULATING RING SHEAR PIN SENSOR No.19 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
Turbine | Limit Switch | A1-15261-650 | ZS0065 | REGULATING RING SHEAR PIN SENSOR No.20 | 3SE5122-0CB01 | 1 | [8 empty] | WL-1-TUR-GVA | TBC | 0
TRV | Limit Switch | A1-15261-650 | ZS0210 | Relief Valve Out Of Step Limit Switch | TK 017-22Y | 1 | [8 empty] | WL-1-RVV | TBC | 0
TRV | Limit Switch | A1-15261-650 | ZS0211 | RELIEF VALVE FULLY CLOSED LIMIT SWITCH | TK 017-22Y | 1 | [8 empty] | WL-1-RVV | TBC | 0
Governor | Prox probe | A1-16123 | ZS1010 | RELAY VALVE | IEC201 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 0
Turbine | Limit Switch | O-60024-UCB4-45 | ZSH0002 | GUIDE VANE UN-LOCKED | TK 017-22Y | 1 | [8 empty] | WL-1-TUR-RGS-ACT | TBC | 0
Brakes and Jacks | Prox Probe | Required has not been redlined yet | ZSH2507 | BRAKES SELECTED INDICATION | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Brakes and Jacks | Prox Probe | A2-07831-250 | ZSH2511 | ALTERNATOR BRAKES & JACKS No.1 POSITION 2 (HIGH) | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Brakes and Jacks | Prox Probe | A2-07831-250 | ZSH2513 | ALTERNATOR BRAKES & JACKS No.3 POSITION 2 (HIGH) | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Turbine | Limit Switch | O-60024-UCB4-45 | ZSL0002 | GUIDE VANE LOCKED | TK 017-22Y | 1 | [8 empty] | WL-1-TUR-RGS-ACT | TBC | 0
Brakes and Jacks | Prox Probe | Required has not been redlined yet | ZSL2507 | JACKS SELECTED INDICATION | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Brakes and Jacks | Prox Probe | A2-07831-250 | ZSL2511 | ALTERNATOR BRAKES & JACKS No.1 POSITION 1 (LOW) | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Brakes and Jacks | Prox Probe | A2-07831-250 | ZSL2512 | ALTERNATOR BRAKES & JACKS No.2 POSITION 1 (LOW) | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Brakes and Jacks | Prox Probe | A2-07831-250 | ZSL2513 | ALTERNATOR BRAKES & JACKS No.3 POSITION 1 (LOW) | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Brakes and Jacks | Prox Probe | A2-07831-250 | ZSL2514 | ALTERNATOR BRAKES & JACKS No.4 POSITION 1 (LOW) | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Nrakes 0-00Jacks | Prox Probe | A2-07831-020 | ZT0030 | TGB SHAFT | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301339
Nrakes 0-00Jacks | Prox Probe | A2-07831-020 | ZT0031 | TGB SHAFT | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301339
Nrakes 0-00Jacks | Prox Probe | A2-07831-020 | ZT0032 | TGB SHAFT | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301339
Nrakes 0-00Jacks | Prox Probe | A2-07831-070 | ZT0091 | ROTOR SHAFT - UPPER | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | 1 | [8 empty] | WL-1-ALT-STR | TBC | 301339
Nrakes 0-00Jacks | Prox Probe | A2-07831-070 | ZT0092 | ROTOR SHAFT - UPPER | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | 1 | [8 empty] | WL-1-ALT-STR | TBC | 301339
Nrakes 0-00Jacks | Prox Probe | A2-07831-060 | ZT0128 | ROTOR SHAFT - LOWER | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | 1 | [8 empty] | WL-1-ALT-STR | TBC | 301339
Nrakes 0-00Jacks | Prox Probe | A2-07831-060 | ZT0129 | ROTOR SHAFT - LOWER | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | 1 | [8 empty] | WL-1-ALT-STR | TBC | 301339
lrakes 1 g feet x 2 400802, Captive Jacks | Prox Probe | O-60024-UCB3-43, A1-15261-652 | ZT0215 | RELIEF VALVE POSITION | RPS0300MD601A01 + 90 Deg Field Installable Connector 560778, Mounting feet x 2 400802, Captive sliding magnet 252182 | 1 | [8 empty] | WL-1-RVV | TBC | 0
0 | LDVT | A1-16119 | ZT1003 | SERVO MOTOR | MT C 0370M N60R 3 A01 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 0
0 | LDVT | A1-16119 | ZT1004 | SERVO MOTOR | MT C 0370M N60R 3 A01 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 0
0 | LDVT | A1-16122 | ZT1005 | PROPORTIONAL CONTROL VALVE | 4WRPEH6CB40L-2X/G24K0/F1M | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 0
0 | LDVT | A1-16120 | ZT1009 | DISTRIBUTING VALVE | RH T 0050M D60 1 A01 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 0
0 | Directional Poppet valve/solenoid | A1-16122 | ZYH1000 | MAIN GOVERNOR SOLENOID VALVE | E-3SE6C7X/F420G125N9K4 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 302900
0 | Directional Poppet valve/solenoid | A1-16122 | ZYH1001 | DUPLICATE GOVERNOR SOLENOID VALVE | E-3SE6C7X/F420G125N9K4 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 302900
0 | ZYH | A3-04891 | ZYH1528 | MAIN OIL PILOT VALVE | 4WE10 D 3X/OFCG24N9K4 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 0
0 | Directional Poppet valve/solenoid | A1-16122 | ZYL1000 | MAIN GOVERNOR SOLENOID VALVE | E-3SE6C7X/F420G125N9K4 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 302900
0 | Directional Poppet valve/solenoid | A1-16122 | ZYL1001 | DUPLICATE GOVERNOR SOLENOID VALVE | E-3SE6C7X/F420G125N9K4 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 302900
0 | ZYL | A3-04891 | ZYL1528 | MAIN OIL PILOT VALVE | 4WE10 D 3X/OFCG24N9K4 | 1 | [8 empty] | WL-1-GOV-CTE | TBC | 0

## Instrumentation
| Project Number |  |  | H-0190022 |  |  |  |  | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
| Project Title |  |  | Wilmot Refurbishment |  |  |  |  | David Van Emmerik |  |  | Date |  |  | 2020-01-31
| Details | [10 empty] | Ordering Information | [5 empty] | SAP & Spare Parts Information
Critical Spare? | Area | Part Type | Device number/P&ID | Drawing Number | Manufacture | Model | Part Number | Part Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
[18 empty] | WL-1-TUR-GVA | 0
| name of location or thing it attaches to | What it is i.e. level sensor, limit switch etc. |  | insert Drawing Number, include sheet number if is has one |  |  | Include Drawing Part Number, if it doesn't have one, just put the manufacturers number | Name of the item i.e. Guide Vane Servo Position Transducer, Guide Vane Lock Open Limit Switch etc. | How may installed | basic details of the device i.e. for a level devices put in its operating perameters i.e. oveall length is 500mm long, measuring range 400mm operating range 4-20ma | Is it a critical spare i.e. without it the amchine won't run, lead time, best place to procure from, previous PO number etc. | [8 empty] | blue = no number found or new number needed
N - quick to replace | Stator enclosure | Thermostat | +ALT-S01 | O-60076-ASH-003 | JUMO | Type AMDR-1 0 to 50 PoPC | 604046-01-021 | Stator Heater thermostat | 1 |  | Stator Heaters cut-out (Alternator Enclosure) | [6 empty] | WL-1-ALT | 0
N - not critical to machine operation | Turbine pit | shaft current coil | 96SC | A2-07831-030 | ROCOIL | 1000 SERIES | 1112 | SHAFT CURRENT/Regosski COIL | 1 |  | NEW - TO BE PURCHASED (2262mm LONG SCREW TOGETHER ENDS) | [6 empty] | WL-1-ALT-SHT | 0
N - not critical to machine operation | Turbine pit | 96SCX | 96SCX | O-60024-UCB4-053 | ROCOIL | Integrator | DIN1 | SHAFT CURRENT COIL Integrator | 4 |  | DIN rail mounted, Single Input 4-20mA output Update P/N where relevant | [6 empty] | WL-1-ALT-SHT | 0
N | Governor | Pressure differential switch | DPS1574 | A1-16122 | HYDAC |  | DF ON 110 M A 5 Y 1.X/B3 | GOVERNOR MANIFOLD FILTER DIFFERNTIAL PRESSURE SWITCH | 1 |  | Governor Supply | [6 empty] | WL-1-GOV-CTE | 0 | possibly 105144 need more detail in sap
Y - Potentially some in store already | Dewatering pump control | PLC | 34DW | F-01820-005-002/003 | Allen Bradley (NHP) |  | 1766-L32BXB | Dewatering PLC | 1 | [8 empty] | WL-S-DW1 | TBC
Y - Already some in store | Dewatering pump control | float switch | LS5000 - LS5006 | GEN-0141-00002-001 | FLYGT |  | ENM-10 float switch | Dewatering Pit Floats | 6 | 30m long as the 20metre is too short | Must be 30 meter cables | [6 empty] | WL-S-DW1 | TBC | 102761
N - Probably already have 125/24V supplies in the store that will work short term until new one ordered if failed | Dewatering pump control | power supply | PS1 | F-01820-005-002/003 | Allen Bradley (NHP) |  | 1606-XLS120E | Power Supply | 1 | [8 empty] | WL-S-DW1 | 0 | 172419
Y - get one spare for both FIT2021 and FIT2133 | Alternator | Flow sensor | FIT2021 | O-60024-UCB4-62, A1-15261-602 | IFM | SA | SA4100 PLUS EVC 561 CABLE (30m), E40258 Progressive Ring Fitting (G1/2 Compression Fitting) | ALTERNATOR BEARING OIL COOLERS RETURN FLOW SENSOR | 1 | [8 empty] | WL-1-ALT-THG-HTX | TBC
Y - get one spare for both FIT2021 and FIT2133 | Alternator | Flow sensor | FIT2133 | O-60024-UCB4-62, A1-15261-510 | IFM | SA | SA4100 PLUS EVC 561 CABLE (30m), E40267 Progressive Ring Fitting (G1/2 Compression Fitting) | TURBINE BEARING OIL COOLERS RETURN FLOW SENSOR | 1 | [8 empty] | WL-1-TUR-GB1-HTX | TBC
Y - Already some replacement heads in store, flow tubes rarely fail so not required? | Alternator | Flow meter | FIT3012 | O-60024-UCB4-50, A1-15261-425 | YOKOGAWA | FLOW TUBE | AFX125G-NNAH1S-AA11-4NB 125mm | ALTERNATOR AIR COOLERS RETURN FLOW METER | 1 |  | Spare read outs already in GP store | [6 empty] | WL-1-CWS-FLR | TBC
Y - Already some replacement heads in store, flow tubes rarely fail so not required? | Switch Yard | Flow meter | FIT3025 | O-60024-UCB4-51, A1-15261-426 | YOKOGAWA | FLOW TUBE | AFX080G-NNAH1S-AA11-4NB 80mm | TRANSFORMER SUPPLY FLOW METER | 1 |  | Spare read outs already in GP store | [6 empty] | WL-1-CWS-FLR | TBC | 300987
Y - Already some replacement heads in store, flow tubes rarely fail so not required? | Alternator floor | Flow meter | FIT3072 | O-60024-UCB4-50, A1-15261-425 | YOKOGAWA | FLOW TUBE | AFX040G-NNAH1S-AA11-4NB 40mm | ALTERNATOR LOWER GUIDE BEARING WATER FLOW RELAY | 1 |  | Spare read outs already in GP store | [6 empty] | WL-1-CWS-FLR | TBC | 303621
Y - Already some replacement heads in store, flow tubes rarely fail so not required? | Turbine pit | Flow meter | FIT3082 | O-60024-UCB4-51, A1-15261-425 | YOKOGAWA | FLOW TUBE | AFX025G-NNAH1S-AA11-4NB 25mm | TURBINE SEAL WATER SUPPLY FLOW METER | 1 |  | Spare read outs already in GP store | [6 empty] | WL-1-CWS-FLR | TBC | 301196
Y - Already some replacement heads in store, flow tubes rarely fail so not required? | Turbine Pit | Flow meter | FIT3095 | O-60024-UCB4-50, A1-15261-425 | YOKOGAWA | FLOW TUBE | AFX040G-NNAH1S-AA11-4NB 40mm | TURBINE GUIDE BEARING OIL COOLER RETURN WATER FLOW METER | 1 |  | Spare read outs already in GP store | [6 empty] | WL-1-CWS-FLR | TBC | 303621
Y - Already some replacement heads in store, flow tubes rarely fail so not required? | Alternator floor | Flow meter | FIT3098 | O-60024-UCB4-50, A1-15261-425 | YOKOGAWA | FLOW TUBE | AFX080G-NNAH1S-AA11-4NB 80mm | ALTERNATOR UPPER GUIDE BEARING OIL COOLERS RETURN FLOW METER | 1 |  | Spare read outs already in GP store | [6 empty] | WL-1-CWS-FLR | TBC | 300987
N | Hill top valve house | surge protection | HLPH-99HH6 | F-01820-016-001/F-01820-017-001 | Critec |  | DINLINE DS-140-2S-150 | Line Protection Devices | 1 | [8 empty] | WL-1-HTV | 0
N - device doesn't exist | Station end | surge protection | HLPS-99HS6 | F-01820-016-001/F-01820-017-001 | Critec |  | DINLINE DS-140-2S-150 | Line Protection Devices | 1
Y - Check stores holding before ordering | HTVH | PLC | 34HH | F-01820-015-002/004 | Allen Bradley (NHP) |  | 1769-L33ER | HTV PLC | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 161761???
Y - Check stores holding before ordering | HTVH | PLC IO card | 34HH | F-01820-015-002/004 | Allen Bradley (NHP) |  | 1769-IF8 | HTV PLC IO cards | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 162237
Y - Check stores holding before ordering | HTVH | PLC IO card | 34HH | F-01820-015-002/004 | Allen Bradley (NHP) |  | 1769-IQ16 | HTV PLC IO cards | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 162211
Y - Check stores holding before ordering | HTVH | PLC IO card | 34HH | F-01820-015-002/004 | Allen Bradley (NHP) |  | 1769-OB16 | HTV PLC IO cards | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 161779
Y - Check stores holding before ordering | HTVH | PLC IO card | 34HH | F-01820-015-002/004 | Allen Bradley (NHP) |  | 1769-PB4 | HTV PLC IO cards | 1 | [8 empty] | WL-1-HTV-CTE | TBC | 162245
N - just end cap | HTVH | PLC IO card | 34HH | F-01820-015-002/004 | Allen Bradley (NHP) |  | 1769-ECR | HTV PLC IO cards | 1 | [8 empty] | WL-1-HTV-CTE | 0 | 162974
N - spares exist in secondary system team | HTVH | PLC IO card | 34HH | F-01820-015-002/004 | Allen Bradley (NHP) |  | MVI69-104S | HTV PLC IO cards | 1 | [8 empty] | WL-1-HTV-CTE | 0 | 171774
Y - Check stores holding before ordering | HTVH | PLC screen | 34HH-PV | F-01820-015-001/004 | Allen Bradley (NHP) |  | 2711P-B7C4D8 | HTV Panel View | 1 | [8 empty] | WL-1-HTV-CTE | TBC
N - indication only, doesn't stop tripping functionality and machine can be run without | HTVH | Pressure transucer | 63HC1 | F-01759 | HYDAC |  | HAD-4745-A-250-00 | HTV Hydraulic Cylinder Pressure Transducer | 1 | [8 empty] | WL-1-HTV-CTE | 0
N - indication only, doesn't stop tripping functionality and machine can be run without | HTVH | Pressure transucer | 63HC2 | F-01759 | HYDAC |  | HAD-4745-A-250-00 | HTV Hydraulic Cylinder Pressure Transducer | 1 | [8 empty] | WL-1-HTV-CTE | 0
N - secondary system team has spares | HTVH | Ethernet switch | 99HTV | F-01820-015-002/004 | Allen Bradley (NHP) |  | 1783-US6T2F | HTV ethernet switch | 1 | [8 empty] | WL-1-HTV-CTE | 0 | 303122
N | HTVH | Fibre switch | 99HTV | F-01820-015-002/004 | Allen Bradley (NHP) |  | 1783-SFP1GLX | HTV switch SFP for SM fibre | 1 | [8 empty] | WL-1-HTV-CTE | 0
N | HTVH | Fibre switch | 99HTV | F-01820-015-002/004 | Allen Bradley (NHP) |  | 1783-SFP1GSX | HTV switch SFP for MM fibre | 1 | [8 empty] | WL-1-HTV-CTE | 0
Y - Check stores holding before ordering - can be used on MIV as well | HTVH | Posistion Transducer | 99HV1 | F-01759-015-023 | CAMILLE BAUER |  | KINAX N702 | HTV Position Transducer | 1 | [8 empty] | WL-1-HTV-CTE | TBC
N | IG | Hooter/siren | H100 | O-60034 page 007 | Allen Bradley (NHP) |  | 855H-B-D30-C-D | Hooters | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-NT1-GT1-CTE | 0
Y - hold one spare in case of failure | IG | level transducers | LT7000, LT7002, LT7003 | A2-07831-700 A3-15261-H285 | Endress & Hauser |  | FMP51-AAACCBLAA4GDJ-LAOC with 21m Rope | Level Transducers (lake, tunnel, trachrack) | 3 |  | 3 off required | [6 empty] | WL-1-NT1-GT1-CTE | TBC
N | IG | Pendant buttons | Pendant Controls | A3-15261-H284 | SCHNEIDER |  | 2 OFF XACA9411 1 OFF XACS101 1 OFF XACS104 | Pendant controls buttons | 2 | [8 empty] | WL-1-NT1-GT1-CTE | 0
Y - Check stores holding before ordering - multiples of these used in station as well | IG | Pressure Transducer | PT9001 | A3-15261-H285 | IFM | PN | PN3092 PLUS EVC 561 CABLE (30m) | Intake Cylinder Oil Pressure | 1 |  | and cable | [6 empty] | WL-1-NT1-GT1-CTE | TBC | 302695 300963(cable)
Y - Check stores holding before ordering - multiples of these used in station as well | IG | Pressure Transducer | PT9002 | A3-15261-H285 | IFM | PN | PN3092 PLUS EVC 561 CABLE (30m) | Intake Pilot Line Oil Pressure | 1 |  | and cable | [6 empty] | WL-1-NT1-GT1-CTE | TBC | 302695 300963(cable)
N | IG | Position indicator | SH28401 | A3-15261-H284 | SCHMERSAL |  | MK-330-11Y-O-O | Bypass Valve Position Indication | 1 | [8 empty] | WL-1-NT1-GT1-CTE | 0
Y - Intake Unable to be operated without this | IG | Position indicator | ZT9000 | A-16338 | MTS | R Series Model 'RP' | RP-S-0900M-D60-1-A01 plus accessories as per drawing +plug | Intake Gate Position | 1 | [8 empty] | WL-1-NT1-GT1-CTE | TBC
| Turbine | Level Indicator | LI0038 | A2-07831-020 | ALEMLUBE | - | FGB2250 Turbine bearing OIL LEVEL SIGHT GUAGE | OIL LEVEL INDICATOR | 1 |  | Have spare sightglass | [6 empty] | WL-1-TUR-GB1 | TBC
| Governor | Level Indicator | LI1585/LI1594 | Include on As-Built | KLINGER | NA | NA | GOVERNOR OIL PRESSURE TANK LEVEL INDICATOR | 1 |  | Re-use Existing Update P/N | [6 empty] | WL-1-GOV-HYD-PV1 | 0
Y - Custom length order long lead time | Governor | Level Switch | LS1570 | A2-07831-100 | PYROSALES | LSP | LSP-1-800-8-1BSP C/F-A | GOVERNOR SUMP TANK OIL LEVEL SWITCH | 1 |  | NEW - TO BE PURCHASED LEVEL PROBE 1" BSP COMPRESSION FITTING, 1 FLOAT L1=625mm OPEN ON RISE | [6 empty] | WL-1-GOV-HYD | TBC
Y - Custom length order long lead time | Turbine | Level Transmitter | LT0036 | O-60024-UCB3-34, A1-15261-510 | MTS | R SERIES MODEL 'RH' | RHH0390MD601A01, COMPLETE WITH FLOAT PART No. 251447 & COLLAR PART No. 56077 + Plug | OIL LEVEL TRANSMITTER FOR TURBINE GUIDE BEARING OIL RESERVOIR | 1 |  | Re-Use Existing | [6 empty] | WL-1-TUR-GB1 | TBC
Y - Custom length order long lead time | Alt Upper Guide | Level Transmitter | LT0500 | A2-07831-070 | MTS | R SERIES MODEL 'RH' | RHM0240MD601A01, COMPLETE WITH FLOAT PART No. 251447 & COLLAR PART No. 56077 + Plug | ALTERNATOR UPPER GUIDE & THRUST BEARING OIL LEVEL TRANSMITTER | 1 | [8 empty] | WL-1-ALT-THG | TBC
Y - Custom length order long lead time | Alt Lower Guide | Level Transmitter | LT0554 | A2-07831-060 | MTS | R SERIES MODEL 'RH' | RHM0240MD601A01, COMPLETE WITH FLOAT PART No. 251447 & COLLAR PART No. 56077 + Plug | ALTERNATOR LOWER GUIDE BEARING OIL LEVEL TRANSMITTER | 1 | [8 empty] | WL-1-ALT-GB1 | TBC
N - long lead time item but machine can run without if required | Governor | Level Transmitter | LT1521 | A2-07831-100 | MTS | LEVEL PLUS SERIES MODEL 'LPR' | LPR1B1B11A0XFICM0800S, COMPLETE WITH FLOAT PART No. 251981-2 | GOVERNOR SUMP TANK OIL LEVEL TRANSMITTER | 1 | [8 empty] | WL-1-GOV-HYD | 0
Y - Custom length order long lead time | Governor | Level Transmitter | LT1522 | A2-07831-100 | MTS | LEVEL PLUS SERIES MODEL 'LPR' | LPR1B1B11A0XFICM01250S, COMPLETE WITH FLOAT PART No. 251981-2 | GOVERNOR OIL PRESSURE TANK OIL LEVEL TRANSMITTER | 1 | [8 empty] | WL-1-GOV-HYD-PV1 | TBC
N - indication only | Tail Race | Level Transmitter | LT7001 | O-60024-SAC-18 | Endress & Hauser | FMR-20 Radar Level Tx | FMR20-AAPBNWDEXR03+R1R8 complete with weather cover and flood protection tubing 3" | Tail Race Level | 1 |  | Measurement range 0-15m | [6 empty] | WL-C-TRC | 0
N - secondary system team has spares | MIV Control Panel | IEC card | X35201 | A1-15261-1000/1001 | Prosoft |  | 5201-DFNT-104S | IEC104 Card | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-MIV-CTE | 0
N - indication only | Alternator | Temp Transmitter | MT0544 | O-60024-UCB4-52, A1-15261-600 | Vaisala | HMT331 | HMT3301 A0A001BCAK100 A0CAABAA | ALTERNATOR ENCLOSURE TEMPERATURE TRANSMITTER | 1 |  | Included in TT0544 |  | Vaisala Pty Ltd. 3 Guest Street Hawthorn Vic. 3122 Ph 03 98156700 Contact: Wayne Nicholson |  |  |  |  | WL-1-ALT | 0
Y - device is common to other sites as well so would make sense to have a spare | Cooling water | Pressure differential | PDT3004 | O-60024-UCB4-53 | Endress & Hauser | PMD55 | 38TUPMD55-AA21BA67LGCHAJA1F Including wall mount bracket for sensor: 71101934 | COOLING WATER SUPPLY DUPLEX FILTER DIFFERENTIAL PRESSURE TRANSDUCER | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-CWS-FLR | TBC
Y - device is common to other sites as well so would make sense to have a spare | Control water | Pressure differential | PDT3004 | O-60024-UCB4-53 | Endress & Hauser | PMD55 | UPMD55-AA21BA67LGCHAJA1F Including wall mount bracket for sensor: 71101934 | CONTROL WATER DUPLEX FILTER DIFFERENTIAL PRESSURE TRANSDUCER | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-MCW-FLT | TBC
| Governor | Accum Pressure Guage | PI1527 | A2-07831-100 | NA | NA | NA | OIL PRESSURE GUAGE | 1 |  | Re-use existing - Refurbed/calibrate | [6 empty] | WL-1-GOV-HYD-PV1-PG1 | 0
| Governor | Pressure Indication | PI1591 | A3-04891 | STAUFF |  | SPG063-040-1-S-B | GOVERNOR MANIFOLD PRESSURE INDICATOR | 1 |  | Governor Supply | [6 empty] | WL-1-GOV-CTE | 0
| Brakes and Jacks | Pressure Indication | PI2518 | Required has not been redlined yet |  |  |  | BRAKES & JACKS PRESSURE INDICATOR (PRESSURE REDUCING VALVE) | 1 |  | Existing | [6 empty] | WL-1-ALT-BJA | 0
| Brakes and Jacks | Pressure Indication | PI2530 | Required has not been redlined yet |  |  |  | BRAKES & JACKS MANUAL JACKING PUMP PRESSURE INDICATOR | 1 |  | Will include in small bore pipework MTO | [6 empty] | WL-1-ALT-BJA | 0
| Brakes and Jacks | Pressure Indication | PI2533 | Required has not been redlined yet |  |  |  | BRAKES & JACKS PRESSURE INDICATOR (BRAKES & JACKS SUMP) | 1 |  | Existing | [6 empty] | WL-1-ALT-BJA | 0
| Alternator | Pressure Indication | PI4500 | A1-16095-001/002 | MAGNEHELIC |  |  | UPPER & LOWER AIR PRESSURE MONITORING MANIFOLD PRESSURE INDICATOR | 1 | [8 empty] | WL-1-ALT-THG | 0
| Alternator | Pressure Indication | PI4501 | A1-16095-001/003 | MAGNEHELIC |  |  | UPPER & LOWER AIR PRESSURE MONITORING MANIFOLD PRESSURE INDICATOR | 1 | [8 empty] | WL-1-ALT-GB1 | 0
Y - hold at least on spare of a PN3092 in store - applicable to multiple sites | Governor | Pressure switch | PS1558 | A2-07831-100 | IFM | PN | PN3092 PLUS EVC 561 CABLE (30m) | GOVERNOR MAIN OIL PUMP PRESSURE SWITCH | 1 | [8 empty] | WL-1-GOV
Y - hold at least on spare of a PN3092 in store - applicable to multiple sites | Governor | Pressure switch | PS1559 | A2-07831-100 | IFM | PN | PN3092 PLUS EVC 561 CABLE (30m) | GOVERNOR STAND-BY OIL PUMP PRESSURE SWITCH | 1 | [8 empty] | WL-1-GOV
Y - applicable to multiple sites | Governor | Pressure switch | PS1568 | A1-16122 | IFM | PV | PV7023 | GOVERNOR MANIFOLD PRESSURE SWITCH | 1 |  | Governor Supply | [6 empty] | WL-1-GOV
Y - applicable to multiple sites | Governor | Pressure switch | PS1569 | A1-16122 | IFM | PV | PV7023 | GOVERNOR MANIFOLD PRESSURE SWITCH | 1 |  | Governor Supply | [6 empty] | WL-1-GOV
Y - hold at least on spare of a PN3092 in store - applicable to multiple sites | Governor | Pressure switch | PS1576 | A1-16122 | IFM | PN | PN3002 (PN3092 as this is discontinued but gov drawing shows PN3002) | GOVERNOR MANIFOLD PRESSURE SWITCH | 1 |  | Governor Supply | [6 empty] | WL-1-GOV
Y - hold at least on spare of a PN3092 in store - applicable to multiple sites | Governor | Pressure switch | PS1580 | O-60024-UCB4-43, A1-15261-252 | IFM | PN | PN3092 PLUS EVC 561 CABLE (30m) | GOVERNOR OIL PRESSURE DOWNSTREAM OF MAIN OIL VALVE | 1 |  | and cable | [6 empty] | WL-1-GOV
Y - hold at least on spare of a PN3071 in store - applicable to multiple sites | Oil Injection | Pressure switch | PS2039 | O-60024-UCB4-27, A1-15261-601 | IFM | PN | PN3071 PLUS EVC 561 CABLE (30m) | OIL INJECTION PUMP PRESSURE SWITCH | 1 |  | and cable | [6 empty] | WL-1-ALT-THG-THR
Y - hold at least on spare of a PN3094 in store - applicable to multiple sites | Brakes and Jacks | Pressure switch | PS2504 | O-60024-UCB4-32,33, A1-15261-525 | IFM | PN | 3094 | BRAKES AIR PRESSURE AVAILABLE PRESSURE SWITCH | 1 | [8 empty] | WL-1-ALT-BJA
Y - hold at least on spare of a PN3071 in store - applicable to multiple sites | Brakes and Jacks | Pressure switch | PS2506 | O-60024-UCB4-32,33, A1-15261-525 | IFM | PN | PN3071 PLUS EVC 561 CABLE (30m) | BRAKES & JACKS OIL PRESSURE SWITCH | 1 |  | and cable | [6 empty] | WL-1-ALT-BJA
Y - hold at least on spare of a PN3094 in store - applicable to multiple sites | Cooling water | Pressure switch | PS3101 | O-60024-CW1-4, O-60024-UCB4-29 | IFM | PN | PN3094 PLUS EVC 561 CABLE (30m) | MAIN COOLING WATER PUMP AT PRESSURE SWITCH | 1 |  | and cable | [6 empty] | WL-1-CWS
Y - hold at least on spare of a PN3094 in store - applicable to multiple sites | Cooling water | Pressure switch | PS3102 | O-60024-CW2-4, O-60024-UCB4-29 | IFM | PN | PN3094 PLUS EVC 561 CABLE (30m) | STANDBY COOLING WATER PUMP AT PRESSURE SWITCH | 1 |  | and cable | [6 empty] | WL-1-CWS
Y - Critical to machine operation - applicable to other sites so hold one spare for multiple station | Turbine | Pressure Transmitter | PT0026 | O-60024-UCB3-33, A1-15261-510 | Endress & Hauser | PMP71 | PMP71-ABA1S111AAEA | SPIRAL CASING PRESSURE TRANSMITTER | 1 | [8 empty] | WL-1-TUR-SPR
N - AMRPD transducer | draft tube | Pressure Transmitter | PT0044 | A2-07831-040 | IFM | PT | PT5494 PLUS EVC 561 CABLE (30m) | DRAFT TUBE PRESSURE TRANSMITTER | 1 |  | and cable | [6 empty] | WL-1-TUR-DTU | 0 | 303130
N - AMRPD transducer | Guide vane | Pressure Transmitter | PT0130 | O-60024-UCB3-041, A1-15261-252 | IFM | PT | PT5443 plus EVC 561 cable 30m | GV SERVOMOTOR OPEN PRESSURE | 1 |  | and cable | [6 empty] | WL-1-TUR-RGS-ACT | 0 | 302366
N - AMRPD transducer | Guide vane | Pressure Transmitter | PT0131 | O-60024-UCB3-041, A1-15261-252 | IFM | PT | PT5443 plus EVC 561 cable 30m | GV SERVOMOTOR CLOSE PRESSURE | 1 | [8 empty] | WL-1-TUR-RGS-ACT | 0 | 302366
N - AMRPD transducer | Turbine | Pressure Transmitter | PT0142 | A2-07831-010 | IFM | PT | PT5443 plus EVC 561 cable 30m | TOP COVER PRESSURE TRANSMITTER | 1 | [8 empty] | WL-1-TUR-COV | 0 | 302366
N - AMRPD transducer | Turbine | Pressure Transmitter | PT0145 | O-60024-UCB3-41, A1-15261-510 | IFM | PT | PT5443 plus EVC 561 cable 30m | SPIRAL CASING PRESSURE TRANSMITTER | 1 | [8 empty] | WL-1-TUR-SPR | 0 | 302366
N - AMRPD transducer | TRV | Pressure Transmitter | PT0216 | O-60024-UCB3-43, A1-15261-652 | IFM | PT | PT5443 PLUS EVC 561 CABLE (30m) | RELIEF VALVE CLOSING PRESSURE | 1 | [8 empty] | WL-1-RVV | 0 | 302366
Y - Critical to machine operation - applicable to other sites so hold one spare for multiple station | Governor | Pressure Transmitter | PT1533 | A2-07831-100 | Endress & Hauser | CERABAR S PMP71 | PMP71-ABA1S111AAEA | GOVERNOR OIL PRESSURE TANK PRESSURE TRANSMITTER | 1 | [8 empty] | WL-1-GOV
N - AMRPD transducer | Governor | Pressure Transmitter | PT1584 | A2-07831-100 | IFM | PT | PT5443 PLUS EVC 561 CABLE (30m) | GOVERNOR OIL PRESSURE TANK PRESSURE TRANSMITTER | 1 | [8 empty] | WL-1-GOV | 0 | 302366
Y - hold at least on spare of a PN3094 in store - applicable to multiple sites | turbine | Pressure Transmitter | PT3314 | O-60024-UCB4-61, A1-15261-510 | IFM | PN | PN3094 PLUS EVC 561 CABLE (30m) | TURBINE SHAFT SEAL COOLING WATER PRESSURE | 1 | [8 empty] | WL-1-CWS | TBC
Y - Critical to machine operation - applicable to other sites so hold one spare for multiple station | TRV | Pressure Transmitter | PT3536 | O-60024-UCB3-33, A1-15261-510 | Endress & Hauser | PMP71 | PMP71-ABA1S111AAEA | MIV/RELIEF VALVE CONTROL WATER PRESSURE | 1 | [8 empty] | WL-1-RVV
N - AMRPD transducer | MIV | Pressure Transmitter | PT3546 | O-60024-UCB4-60, A1-15261-510 | IFM | PT | PT5443 PLUS EVC 561 CABLE (30m) | MIV SERVO 1 CLOSE PRESSURE | 1 | [8 empty] | WL-1-MIV-CTE | 0 | 302366
N - AMRPD transducer | MIV | Pressure Transmitter | PT3547 | O-60024-UCB4-60, A1-15261-510 | IFM | PT | PT5443 PLUS EVC 561 CABLE (30m) | MIV SERVO 1 OPEN PRESSURE | 1 | [8 empty] | WL-1-MIV-CTE | 0 | 302366
N - AMRPD transducer | Turbine | Pressure Transmitter | PT3585 | O-60024-UCB3-43, A1-15261-510 | IFM | PT | PT5443 plus EVC 561 cable 30m | Penstock Pressure (AMRPD) | 1 | [8 empty] | WL-1-PP1 | 0 | 302366
N - AMRPD transducer | MIV | Pressure Transmitter | PT3613 | A0-00227 | IFM | PT | PT5443 PLUS EVC 561 CABLE (30m) | SERVICE SEAL ON PRESSURE | 1 | [8 empty] | WL-1-MIV-CTE | 0 | 302366
N - AMRPD transducer | MIV | Pressure Transmitter | PT3614 | A0-00227 | IFM | PT | PT5443 PLUS EVC 561 CABLE (30m) | SERVICE SEAL OFF PRESSURE | 1 | [8 empty] | WL-1-MIV-CTE | 0 | 302366
N - AMRPD transducer | MIV | Pressure Transmitter | PT3646 | O-60024-UCB4-60, A1-15261-510 | IFM | PT | PT5443 PLUS EVC 561 CABLE (30m) | MIV SERVO 2 CLOSE PRESSURE | 1 | [8 empty] | WL-1-MIV-CTE | 0 | 302366
N - AMRPD transducer | MIV | Pressure Transmitter | PT3647 | O-60024-UCB4-60, A1-15261-510 | IFM | PT | PT5443 PLUS EVC 561 CABLE (30m) | MIV SERVO 2 OPEN PRESSURE | 1 | [8 empty] | WL-1-MIV-CTE | 0 | 302366
N - not critical to machine operation | Switch Yard | Prox Prob | 33EA | O-60024-UCB4-31, A1-15261-405 | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | Earth Switch Open Indication | 1 |  | Mount to be fabricated by site crew for these | [6 empty] | WL-1-SGR | 0 | 166836
N - not critical to machine operation | Switch Yard | Prox Prob | 33EB | O-60024-UCB4-31, A1-15261-405 | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | Earth Switch Closed Indication | 1 |  | Mount to be fabricated by site crew for these | [6 empty] | WL-1-SGR | 0 | 166836
N | SAC panel | Hooter/siren | H01 | O-60024-UCB1-027 | Allen Bradley (NHP) |  | 855H-B-D30-C-D | Hooters | 1 | [9 empty] | 0
Y - critical to machine operation - not transferrable to other machines due to different sizes | Turbine BRG | RTD | TE0028 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's | TGB PAD RTD | 1 | [8 empty] | WL-1-TUR-GB1 | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Turbine BRG | RTD | TE0029 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's | TGB PAD RTD | 1 | [8 empty] | WL-1-TUR-GB1 | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Turbine BRG | RTD | TE0035 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's | TGB SUMP RTD | 1 | [8 empty] | WL-1-TUR-GB1 | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Turbine BRG | RTD | TE0070 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's | TGB PAD RTD | 1 | [8 empty] | WL-1-TUR-GB1 | TBC
N - indication only | Brushgear | RTD | TE0182 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's | BRUSHGEAR ENCLOSURE TEMPERATURE | 1 | [8 empty] | WL-1-EXS-BGR | 0
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator Thrust Brg | RTD | TE0501 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR UPPER THRUST BEARING PAD TEMPERATURE | 1 | [8 empty] | WL-1-ALT-THG-THR | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator Thrust Brg | RTD | TE0502 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR UPPER THRUST BEARING PAD TEMPERATURE | 1 | [8 empty] | WL-1-ALT-THG-THR | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator Thrust Brg | RTD | TE0503 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR UPPER THRUST BEARING PAD TEMPERATURE | 1 | [8 empty] | WL-1-ALT-THG-THR | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator Thrust Brg | RTD | TE0504 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR UPPER THRUST BEARING PAD TEMPERATURE | 1 | [8 empty] | WL-1-ALT-THG-THR | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator upper guide brg | RTD | TE0506 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | THERMOMETER FOR BEARING SHELL | 1 |  | 90deg bend | [6 empty] | WL-1-ALT-THG-GB1 | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator upper guide brg | RTD | TE507 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | THERMOMETER FOR BEARING SHELL | 1 |  | 90deg bend | [6 empty] | WL-1-ALT-THG-GB1 | TBC
N - standard PT100 | Alternator upper guide brg | RTD | TE0508 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | OIL TEMPERATURE (SUMP) | 1 | [8 empty] | WL-1-ALT-THG-GB1 | 0
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator upper guide brg | RTD | TE0509 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | THERMOMETER FOR BEARING SHELL | 1 |  | 90deg bend | [6 empty] | WL-1-ALT-THG-GB1 | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator upper guide brg | RTD | TE0510 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | THERMOMETER FOR BEARING SHELL | 1 |  | 90deg bend | [6 empty] | WL-1-ALT-THG-GB1 | TBC
N - standard PT100 | Alternator | RTD | TE0521 | Andritz Drawing 300865108 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR AIR COOLERS TEMPERATURE (HOT SIDE) | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-HTX | 0
N - standard PT100 | Alternator | RTD | TE0522 | Andritz Drawing 300865108 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR AIR COOLERS TEMPERATURE (COLD SIDE) | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-HTX | 0
N - standard PT100 | Alternator | RTD | TE0523 | Andritz Drawing 300865108 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR AIR COOLERS TEMPERATURE (HOT SIDE) | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-HTX | 0
N - standard PT100 | Alternator | RTD | TE0524 | Andritz Drawing 300865108 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR AIR COOLERS TEMPERATURE (COLD SIDE) | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-HTX | 0
N | Alternator | RTD | TE0525 | Andritz Drawing 300865154 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR STATOR TEMPERATURE | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-STR | 0
N | Alternator | RTD | TE0526 | Andritz Drawing 300865154 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR STATOR TEMPERATURE | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-STR | 0
N | Alternator | RTD | TE0527 | Andritz Drawing 300865154 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR STATOR TEMPERATURE | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-STR | 0
N | Alternator | RTD | TE0528 | Andritz Drawing 300865154 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR STATOR TEMPERATURE (CORE TOOTH) | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-STR | 0
N | Alternator | RTD | TE0529 | Andritz Drawing 300865154 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR STATOR TEMPERATURE (CORE) | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-STR | 0
N | Alternator | RTD | TE0530 | Andritz Drawing 300865154 | PH. SCHENK | PT100 | PT100, SIMPLEX RTD | ALTERNATOR STATOR TEMPERATURE | 1 |  | Andritz supply | [6 empty] | WL-1-ALT-STR | 0
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator Lower guide brg | RTD | TE0550 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR LOWER GUIDE BEARING RTD | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-GB1 | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator Lower guide brg | RTD | TE0551 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR LOWER GUIDE BEARING RTD | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-GB1 | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator Lower guide brg | RTD | TE0552 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR LOWER GUIDE BEARING RTD | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-GB1 | TBC
Y - critical to machine operation - not transferrable to other machines due to different sizes | Alternator Lower guide brg | RTD | TE0556 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR LOWER GUIDE BEARING OIL RTD | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-GB1 | TBC
N - alarm only | Governor | RTD | TE1520 | A2-07831-100 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | GOVERNOR SUMP TANK OIL RTD | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-GOV-HYD | 0
Y - hold one spare | Alternator Bearing Cooler | RTD | TE2018 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR BEARING OIL COOLERS SUPPLY TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-THG-HTX | TBC
Y - hold one spare | Alternator Bearing Cooler | RTD | TE2019 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR BEARING OIL COOLERS RETURN TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-THG-HTX | TBC
Y - hold one spare | Alternator Bearing Cooler | RTD | TE2020 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR BEARING OIL COOLERS RETURN TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-THG-HTX | TBC
Y - hold one spare for all cooling water pipes | cooling water | RTD | TE3002 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | COOLING WATER SUPPLY TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-CWS | TBC
Y - hold one spare for all cooling water pipes | Alternator Coolers | RTD | TE3011 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR AIR COOLERS RETURN TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-CWS | TBC
Y - hold one spare for all cooling water pipes | Transformer coolers | RTD | TE3019 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | TRANSFORMER SUPPLY TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-CWS | TBC
Y - hold one spare for all cooling water pipes | Transformer coolers | RTD | TE3020 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | TRANSFORMER SUPPLY TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-CWS | TBC
Y - hold one spare for all cooling water pipes | Alternator Lower guide brg | RTD | TE3071 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR LOWER GUIDE BEARING RETURN WATER TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-CWS | TBC
Y - hold one spare for all cooling water pipes | Turbine BRG | RTD | TE3084 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | TURBINE GUIDE BEARING OIL COOLER RETURN WATER TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-CWS | TBC
Y - hold one spare for all cooling water pipes | Alternator Bearing Cooler | RTD | TE3097 | A2-07831-002 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's (0-100deg C) | ALTERNATOR BEARING OIL COOLERS RETURN TEMPERATURE | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-CWS | TBC
Y - hold one spare for all cooling water pipes | Intake | RTD | TE9020 | C-08667 | TEMTROL TECHNOLOGIES | PT100 | PT100, DUPLEX RTD's | Intake Gate Sump RTD | 1 |  | Approx. 300mm long is required - may need a poper drawing or I can come up with details steve? | [6 empty] | WL-1-NT1-GT1-CTE | TBC
N - indication/alarm only | Brushgear | Infrared Temperature | TT0180 | O-60024-UCB4-52 | RAYTEK | MI3 | RAYMI320LTSCB15 (Infrared Temperature Sensor with 15m cable, 22:1 Optics, 0 to 1000 degrees C) and RAYMI3COMM (Infrared Thermometer Communication box with USB 2.0 Communications) Complete with window XXMI3ACPWP (65decC ambient) | BRUSHGEAR IR TEMPERATURE SENSOR No.1 | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-EXS-BGR | 0
N - indication/alarm only | Brushgear | Infrared Temperature | TT0181 | O-60024-UCB4-52 | RAYTEK | MI3 | RAYMI320LTSCB15 (Infrared Temperature Sensor with 15m cable, 22:1 Optics, 0 to 1000 degrees C) and RAYMI3COMM (Infrared Thermometer Communication box with USB 2.0 Communications) Complete with window XXMI3ACPWP (65decC ambient) | BRUSHGEAR IR TEMPERATURE SENSOR No.2 | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-EXS-BGR | 0
N - indication/alarm only | Alternator | Moisture transmitter | TT0544 | O-60024-UCB4-52 | Vaisala | HMT331 | HMT3301 A0A001BCAK100 A0CAABAA | ALTERNATOR ENCLOSURE MOISTURE TRANSMITTER | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT | 0
N - indication only | Station | RTD | TT7010 | O-60024-UCB4-41 | TEMTROL TECHNOLOGIES | PT100 | DUPLEX RTD's (0-100deg C) | Station Ambient Temperature | 1 |  | As per A2-07831-002 inlcuding APAQ-HRF (70APHRF001) | [6 empty] | WL-1 | 0
Y - hold common spares in store for multiple stations | Turbine | Vibration Accelerometer | VE0025 | A2-07831-010 | PCB | 626B02 | 2 pin MIL-C-5015 wireable socket to match, low freq. industrical ceramic shear ICP accelerometer 500mV/g | TOP COVER VIBRATION | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-TUR-GB1 | TBC | 401538
Y - hold common spares in store for multiple stations | Turbine | Vibration Accelerometer | VE0033 | A2-07831-020 | PCB | 626B02 |  | TGB VIBRATION | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-TUR-GB1 | TBC | 401538
Y - hold common spares in store for multiple stations | Turbine | Vibration Accelerometer | VE0034 | A2-07831-020 | PCB | 626B02 |  | TGB VIBRATION | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-TUR-GB1 | TBC | 401538
Y - hold common spares in store for multiple stations | Alternator Lower guide brg | Vibration Accelerometer | VE0078 | A2-07831-060 | PCB | 626B02 |  | ALTERNATOR LOWER GUIDE BEARING VIBRATION | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-GB1 | TBC | 401538
Y - hold common spares in store for multiple stations | Alternator Lower guide brg | Vibration Accelerometer | VE0079 | A2-07831-060 | PCB | 626B02 |  | ALTERNATOR LOWER GUIDE BEARING VIBRATION | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-GB1 | TBC | 401538
Y - hold common spares in store for multiple stations | Alternator upper guide/Thust brg | Vibration Accelerometer | VE0088 | A2-07831-070 | PCB | 626B02 |  | ALTERNATOR UPPER GUIDE & THRUST BEARING VIBRATION | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-THG | TBC | 401538
Y - hold common spares in store for multiple stations | Alternator upper guide/Thust brg | Vibration Accelerometer | VE0089 | A2-07831-070 | PCB | 626B02 |  | ALTERNATOR UPPER GUIDE & THRUST BEARING VIBRATION | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-THG | TBC | 401538
Y - hold common spares in store for multiple stations | Alternator upper guide/Thust brg | Vibration Accelerometer | VE0090 | A2-07831-070 | PCB | 626B02 |  | ALTERNATOR UPPER GUIDE & THRUST BEARING VIBRATION | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-THG | TBC | 401538
Y - hold common spares in store for multiple stations | Turbine Shaft | Speed Sensor | ZS0006 | A2-07831-020/30 | JAQUET | DSF 1210.00 STV 5m | 374Z-03870 | POLE BAND SPEED SENSOR | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-TUR-SHT | TBC | 301815
Y - hold common spares in store for multiple stations | Turbine Shaft | Speed Sensor | ZS0007 | A2-07831-020/30 | JAQUET | DSF 1210.00 STV 5m | 374Z-03870 | POLE BAND SPEED SENSOR | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-TUR-SHT | TBC | 301815
Y - hold common spares in store for multiple stations | Turbine Shaft | Speed Sensor | ZS0008 | A2-07831-020/30 | JAQUET | DSF 1210.00 STV 5m | 374Z-03870 | POLE BAND SPEED SENSOR | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-TUR-SHT | TBC | 301815
Y - hold common spares in store for multiple stations | Turbine Shaft | Speed Sensor | ZS0009 | A2-07831-020/30 | JAQUET | DSF 1210.00 STV 5m | 374Z-03870 | POLE BAND SPEED SENSOR | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-TUR-SHT | TBC | 301815
Y - hold common spares in store for multiple stations | Turbine Shaft | Speed Sensor | ZS0010 | A2-07831-020/30 | JAQUET | DSF 1210.00 STV 5m | 374Z-03870 | POLE BAND SPEED SENSOR | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-TUR-SHT | TBC | 301815
|  | ZS | 22 |  |  |  |  | SERVO MOTOR Closed Limit Switch | 1 |  | No longer needed
|  | ZS | 24 |  |  |  |  | SERVO MOTOR No Load Limit Switch | 1 |  | No longer needed
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0046 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.1 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0047 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.2 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0048 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.3 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0049 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.4 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0050 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.5 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0051 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.6 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0052 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.7 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0053 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.8 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0054 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.9 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0055 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.10 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0056 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.11 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0057 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.12 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0058 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.13 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0059 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.14 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0060 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.15 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0061 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.16 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0062 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.17 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0063 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.18 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0064 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.19 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - hold common spares in store for multiple stations | Turbine | Limit Switch | ZS0065 | A1-15261-650 | SIEMENS | Sirius Position Switch | 3SE5122-0CB01 | REGULATING RING SHEAR PIN SENSOR No.20 | 1 | [8 empty] | WL-1-TUR-GVA | TBC
Y - long lead time items hold at least on spare | TRV | Limit Switch | ZS0210 | A1-15261-650 | SCHMERSAL |  | TK 017-22Y | Relief Valve Out Of Step Limit Switch | 1 | [8 empty] | WL-1-RVV | TBC
Y - long lead time items hold at least on spare | TRV | Limit Switch | ZS0211 | A1-15261-650 | SCHMERSAL |  | TK 017-22Y | RELIEF VALVE FULLY CLOSED LIMIT SWITCH | 1 | [8 empty] | WL-1-RVV | TBC
Y | Governor | Prox probe | ZS1010 | A1-16123 | IFM | IEC | IEC201 | RELAY VALVE | 1 | [8 empty] | WL-1-GOV-CTE | TBC
N | Brakes and Jacks | Solenoid valve | ZS2502 | Required has not been redlined yet | ASCO |  | SCB223A103V 24VDC | BRAKES APPLIED SOLENOID VALVE | 1 |  | Tom G to redline drawings as built | [6 empty] | WL-1-ALT-BJA | 0
Y - long lead time items hold at least on spare | Turbine | Limit Switch | ZSH0002 | O-60024-UCB4-45 | SCHMERSAL | Snap-Lock Limit Switch | TK 017-22Y | GUIDE VANE UN-LOCKED | 1 | [8 empty] | WL-1-TUR-RGS-ACT | TBC
Y - hold common spares in store for multiple stations | Brakes and Jacks | Prox Probe | ZSH2507 | Required has not been redlined yet | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | BRAKES SELECTED INDICATION | 1 |  | Tom G to redline drawings as built | [6 empty] | WL-1-ALT-BJA | TBC | 166836
Y - hold common spares in store for multiple stations | Brakes and Jacks | Prox Probe | ZSH2511 | A2-07831-250 | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | ALTERNATOR BRAKES & JACKS No.1 POSITION 2 (HIGH) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Y - hold common spares in store for multiple stations | Brakes and Jacks | Prox Probe | ZSH2513 | A2-07831-250 | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | ALTERNATOR BRAKES & JACKS No.3 POSITION 2 (HIGH) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
| Turbine | Limit Switch | ZSL0002 | O-60024-UCB4-45 | SCHMERSAL | Snap-Lock Limit Switch | TK 017-22Y | GUIDE VANE LOCKED | 1 | [8 empty] | WL-1-TUR-RGS-ACT | TBC
Y - hold common spares in store for multiple stations | Brakes and Jacks | Prox Probe | ZSL2507 | Required has not been redlined yet | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | JACKS SELECTED INDICATION | 1 |  | Tom G to redline drawings as built | [6 empty] | WL-1-ALT-BJA | TBC | 166836
Y - hold common spares in store for multiple stations | Brakes and Jacks | Prox Probe | ZSL2511 | A2-07831-250 | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | ALTERNATOR BRAKES & JACKS No.1 POSITION 1 (LOW) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Y - hold common spares in store for multiple stations | Brakes and Jacks | Prox Probe | ZSL2512 | A2-07831-250 | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | ALTERNATOR BRAKES & JACKS No.2 POSITION 1 (LOW) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Y - hold common spares in store for multiple stations | Brakes and Jacks | Prox Probe | ZSL2513 | A2-07831-250 | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | ALTERNATOR BRAKES & JACKS No.3 POSITION 1 (LOW) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Y - hold common spares in store for multiple stations | Brakes and Jacks | Prox Probe | ZSL2514 | A2-07831-250 | IFM | IFW201 | IFW201 (M12, RANGE: 8mm NON-FLUSH MOUNTABLE, PLUS EVT396 Right Angled Plug CABLE (30m) | ALTERNATOR BRAKES & JACKS No.4 POSITION 1 (LOW) | 1 | [8 empty] | WL-1-ALT-BJA | TBC | 166836
Y - hold common spares in store for multiple stations | Nrakes 0-00Jacks | Prox Probe | ZT0030 | A2-07831-020 | Bentley Nevada | 3300 XL SERIES | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | TGB SHAFT | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301339
Y - hold common spares in store for multiple stations | Nrakes 0-00Jacks | Prox Probe | ZT0031 | A2-07831-020 | Bentley Nevada | 3300 XL SERIES | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | TGB SHAFT | 1 | [8 empty] | WL-1-TUR-SHT | TBC | 301339
Y - hold common spares in store for multiple stations | Nrakes 0-00Jacks | Prox Probe | ZT0032 | A2-07831-020 | Bentley Nevada | 3300 XL SERIES | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | TGB SHAFT | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-TUR-SHT | TBC | 301339
Y - hold common spares in store for multiple stations | Nrakes 0-00Jacks | Prox Probe | ZT0091 | A2-07831-070 | Bentley Nevada | 3300 XL SERIES | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | ROTOR SHAFT - UPPER | 1 |  | NEW - TO BE PURCHASED | [6 empty] | WL-1-ALT-STR | TBC | 301339
Y - hold common spares in store for multiple stations | Nrakes 0-00Jacks | Prox Probe | ZT0092 | A2-07831-070 | Bentley Nevada | 3300 XL SERIES | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | ROTOR SHAFT - UPPER | 1 |  | NEW - TO BE PURCHASED - Assume it is correct number not found in DG Scope | [6 empty] | WL-1-ALT-STR | TBC | 301339
Y - hold common spares in store for multiple stations | Nrakes 0-00Jacks | Prox Probe | ZT0128 | A2-07831-060 | Bentley Nevada | 3300 XL SERIES | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | ROTOR SHAFT - LOWER | 1 |  | NEW - TO BE PURCHASED - Assume it is correct number not found in DG Scope | [6 empty] | WL-1-ALT-STR | TBC | 301339
Y - hold common spares in store for multiple stations | Nrakes 0-00Jacks | Prox Probe | ZT0129 | A2-07831-060 | Bentley Nevada | 3300 XL SERIES | 330104-00-05-90-01-00 PROBE 3300 8MM BENTLY M10X1 ARM, 330180-91-00 3300 XL PROXIMITOR | ROTOR SHAFT - LOWER | 1 |  | NEW - TO BE PURCHASED - Assume it is correct number not found in DG Scope | [6 empty] | WL-1-ALT-STR | TBC | 301339
Y - long lead time item and custom length | lrakes 1 g feet x 2 400802, Captive Jacks | Prox Probe | ZT0215 | O-60024-UCB3-43, A1-15261-652 | MTS | R SERIES MODEL 'RP' | RPS0300MD601A01 + 90 Deg Field Installable Connector 560778, Mounting feet x 2 400802, Captive sliding magnet 252182 | RELIEF VALVE POSITION | 1 |  | Need to update stroke length once have a drawing | [6 empty] | WL-1-RVV | TBC
Y - long lead time item and custom length |  | LDVT | ZT1003 | A1-16119 | THERMOFISHER SCIENTIFIC (MTS) | MH Series Model 'MT' | MT C 0370M N60R 3 A01 | SERVO MOTOR | 1 |  | Governor Supply - Servo LDVT | [6 empty] | WL-1-GOV-CTE | TBC
Y - long lead time item and custom length |  | LDVT | ZT1004 | A1-16119 | THERMOFISHER SCIENTIFIC (MTS) | MH Series Model 'MT' | MT C 0370M N60R 3 A01 | SERVO MOTOR | 1 |  | Governor Supply - Servo LDVT | [6 empty] | WL-1-GOV-CTE | TBC
Y - long lead time item and custom length |  | LDVT | ZT1005 | A1-16122 | REXROTH |  | 4WRPEH6CB40L-2X/G24K0/F1M | PROPORTIONAL CONTROL VALVE | 1 |  | Governor Supply | [6 empty] | WL-1-GOV-CTE | TBC
Y - long lead time item and custom length |  | LDVT | ZT1009 | A1-16120 | THERMOFISHER SCIENTIFIC (MTS) | RH Series Model 'RH' | RH T 0050M D60 1 A01 | DISTRIBUTING VALVE | 1 |  | Governor Supply - Distributing Valve Position | [6 empty] | WL-1-GOV-CTE | TBC
? - already should have spares in store? |  | Directional Poppet valve/solenoid | ZYH1000 | A1-16122 | REXROTH |  | E-3SE6C7X/F420G125N9K4 | MAIN GOVERNOR SOLENOID VALVE | 1 |  | Governor Supply | [6 empty] | WL-1-GOV-CTE | TBC | 302900
? - already should have spares in store? |  | Directional Poppet valve/solenoid | ZYH1001 | A1-16122 | REXROTH |  | E-3SE6C7X/F420G125N9K4 | DUPLICATE GOVERNOR SOLENOID VALVE | 1 |  | Governor Supply | [6 empty] | WL-1-GOV-CTE | TBC | 302900
|  | ZYH | ZYH1528 | A3-04891 | REXROTH | MNR: R983031009 | 4WE10 D 3X/OFCG24N9K4 | MAIN OIL PILOT VALVE | 1 |  | Labeled as SH1585 | [6 empty] | WL-1-GOV-CTE | TBC
? - already should have spares in store? |  | Directional Poppet valve/solenoid | ZYL1000 | A1-16122 | REXROTH |  | E-3SE6C7X/F420G125N9K4 | MAIN GOVERNOR SOLENOID VALVE | 1 |  | Governor Supply | [6 empty] | WL-1-GOV-CTE | TBC | 302900
? - already should have spares in store? |  | Directional Poppet valve/solenoid | ZYL1001 | A1-16122 | REXROTH |  | E-3SE6C7X/F420G125N9K4 | DUPLICATE GOVERNOR SOLENOID VALVE | 1 |  | Governor Supply | [6 empty] | WL-1-GOV-CTE | TBC | 302900
|  | ZYL | ZYL1528 | A3-04891 | REXROTH | MNR: R983031009 | 4WE10 D 3X/OFCG24N9K4 | MAIN OIL PILOT VALVE | 1 |  | Labled as SL1585 | [6 empty] | WL-1-GOV-CTE | TBC
N | turbine shaft | Pole Band | NA | A2-07831-030/-020 | JAQUET | FTP 555 | 120 TEETH, SHAFT DIA406mm | POLE BAND | 1 | Not Installed | Spare | [6 empty] | WL-1-TUR-SHT | 0
N | turbine shaft | Toothed wheel | NA | A3-05099 |  |  |  | POLE BAND/toothed wheel assembly | 1 |  | This is the one Installed | [6 empty] | WL-1-TUR-SHT | 0
Note on T157: Tom Goddard: Qty for all 20 GV's

## Guide Vanes
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | Comments | General Information | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Guide Vane Lever | Fastener | O-27672 | N/A | Guide Vane Adjusting Liner Bolt (Centre Bolt) | M20 x 65 Hex Head Bolt, Class 4.6, Z/P | 20 |  |  | Y | Site | Josh | Y |  | Tub 1 | WL-1-TUR-GVA | 0
Guide Vane Lever | Tab Washer | O-25959 | N/A | Guide Vane Adjusting Liner Bolt Locking Tab (Centre Bolt) | 20mm Nordlock Washer Z/P | 20 |  |  | Y | Site | Josh | Y |  | Tub 1 | WL-1-TUR-GVA | 0
Guide Vane Lever | Component | O-25959 | 1 | Guide Vane | Guide Vane | 20 |  | See drawing O-27255 for manufacturing details | Y | S&W | Matt | N/A | Y | Loading Bay | WL-1-TUR-GVA | 0
Guide Vane Lever | Component | O-25959 | 2 | Guide Vane Lever | Guide Vane Lever | 20 |  | See drawing O-27254 for manufacturing details | Y | S&W | Matt | N/A |  | S&W | WL-1-TUR-GVA | 0
Guide Vane Lever | Fastener | O-27672 | N/A | Guide Vane Centre Cap Bolts | M16 x 40 Hex Head Bolt, Class 4.6, Z/P | 80 |  | Not shown on any drawing | Y | Site | Josh | Y |  | Tub 1 | WL-1-TUR-GVA | 0
Guide Vane Lever | Tab Washer | O-27672 | N/A | Guide Vane Centre Cap Bolt Nordlock | 16mm Nordlock Washer Z/P | 80 | Bolt to now be fitted with Nordlocks | Not shown on any drawing, Nordlock to be fitted | Y | Site | Josh | Y |  | Tub 1 | WL-1-TUR-GVA | 0
Guide Vanes | Component | O-27255 |  | Guide Vane | Guide Vane | 20 |  | See drawing O-25959 for assembly details | Y | S&W | Matt |  |  | N/A | WL-1-TUR-GVA | 0
Guide Vane Lever | Component | O-27672 | N/A | Guide Vane Centre Cap | Guide Vane Centre Cap | 20 | Not referenced on any drawing | Not referenced on any drawing | Y | S&W | Matt | N/A |  | S&W | WL-1-TUR-GVA | 0
Guide Vanes | Component | O-27254 |  | Guide Vane Lever | Guide Vane Lever | 20 |  | See drawing O-25959 for assembly details | Y | S&W | Matt |  |  | N/A | WL-1-TUR-GVA | 0
Guide Vanes | Component | O-60620/O-60621 | N/A | Guide Vane Lever Lower Part | Premachined, lower part (thrust surface) of guide vane lever | 20 |  | New design from refurbishment | [6 empty] | WL-1-TUR-GVA | 6
Guide Vane Lever | Component | O-27672/O-60600 | N/A | Guide Vane Key | Gib Head Key - AS 3678-250 Plate | 20 | Will there be a new drawing for this? | Used to pin the Guide Vane to the Leaver, Not referenced on any drawing | Y | S&W | Matt | N/A |  | Tub 1 | WL-1-TUR-GVA | 5
Guide Vane Lever | Component | O-27672/O-60600 | N/A | Guide Vane Adjusting Liner | Adjusting Liner for setting Centre Height - AS 3678-250 | 20 | Will there be a new drawing for this? | Used to set the position within the Check Plates, Not referenced on any drawing | Y | S&W | Matt | N/A |  | Tub 1 | WL-1-TUR-GVA | 20
Guide Vane Link | Component | O-25959 | 7 | Shear Pin | New in equiv. to ASTM 1035 | 20 | Will there be a new drawing for this? | See drawing O-60610 for manufacturing details | Y | Voith | Matt | N/A |  | Tub 5 | WL-1-TUR-GVA | 23 (10 left at WL Site)
Guide Vane Link | Bearing | O-25959 | 8 | Guide Vane Link Bush | DU Bearings Zinc Plated Backing | 40 | Will there be a new drawing for this? Are there spares? | For use with both the Link Pin and Shear Pin and is to be installed in the Guide Vane Link | Y | Voith | Matt | N/A |  | ? | WL-1-TUR-GVA | 10
Guide Vane Link | Component | O-25959 | 9 | Shear Pin Monitoring Device | Fixed Pin, Ø3 | 20 |  | O-27870 | Y | S&W | Matt | N/A |  | Tub 2 | WL-1-TUR-GVA | 32
Guide Vane Link | Component | O-25959 | 10 | Shear Pin Monitoring Device | Moving Pin | 20 |  | Reuse. S&W | Y | S&W | Matt | N/A |  | Tub 2 | WL-1-TUR-GVA | 0
Guide Vane Link | Component | O-24973 | N/A | Shear Pin Monitoring Device | Limit Switch and Cam Assembly | 20 | Is the limit switch assembly refurbish by S&W? |  | N | Site | Tom | N |  | Tub 2 | WL-1-TUR-GVA | 0
Guide Vane Link | Fastener | O-27254 | N/A | Shear Pin Monitoring Device Bolts | M8 x 25mm Capscrews, Class 12.9 | 120 |  |  | Y | Site | Josh | Y |  | Tub 2 | WL-1-TUR-GVA | 0
Guide Vane Link | Component | O-25959 | 11 | Guide Vane Link | Turnbuckle style Link | 20 |  |  | Y | S&W | Matt | N/A |  | ? | WL-1-TUR-GVA | 0
Guide Vane Link | Component | O-25959 | 12 | Guide Vane Link Pin | Link Pin (fixed), Ø40 | 20 | Supplied new in SS | O-27866 Installed in the Regulating Ring, spares premachined | Y | Voith | Matt | N/A |  | Tub 5 | WL-1-TUR-GVA | 5
Guide Vane Link | Component | O-25959 | 13 | Link Pin and Shear Pin Keeper Plates | Reuse - 10 mm Steel Plate | 40 | Will this be painted? | Used to secure the Link Pin and Shear Pin and prevent rotation | Y | S&W | Matt | N/A |  | Tub 2 | WL-1-TUR-GVA | 0
Guide Vane Link | Fastener | O-27254 | N/A | Link Pin and Shear Pin Keeper Plate Bolts | M6 x 20mm Hex Head Bolt, Class 4.6 Z/P | 80 | Length increased by 5mm to account for Nordlock | Used to secure the Keeper Plates in position. | Y | Site | Josh | Y |  | Tub 2 | WL-1-TUR-GVA | 0
Guide Vane Link | Tab Washer | O-27255 | N/A | Link Pin and Shear Pin Keeper Plate Bolt Nordlock | 6mm Nordlock Washer Z/P | 80 | Locking Tab replaced with Nordlock | Not shown on any drawing, use Nordlock | Y | Site | Josh | Y |  | Tub 2 | WL-1-TUR-GVA | 0
Guide Vane Link | Device | O-25959 | 14 | Guide Vane Shear Pin Limit Switch | Enter new details? | 20 | Pat to sort |  | Y | Site | Pat | Y |  | Tub 2 | WL-1-TUR-GVA | 0
Upper Bearing Housing | Bearing | O-25959 / O-60600 | 5 | Lower Thurst Bearing Liner | Deva Tex | 20 | Will there be a new drawing for this? Are there spares? Supplied fit to housing and final machined to 0.03 flatness, 1.6 Ra | They are to be adhered to the Upper Bearing Housing - See O-60259 | Y | S&W | Matt | N/A |  | Installed in Upper Bearing Housing | WL-1-TUR-GVA | 5
Lower Bearing Housing | Seal | O-27672 / O-60600 | N/A | Lower Bearing Housing Top Outer Seal | P140 NBR70 O'Ring (139.6mm x 5.7mm) | 20 | Confirmed as-built |  | Y | Site | Tom | N |  | Tub 3 | WL-1-TUR-GVA | 2
Lower Bearing Housing | Seal | O-27672 / O-60600 | N/A | Lower Guide Vane Shaft Seal | P90 NBR70 O'Ring (89.6mm x 5.7mm) | 20 | Confirmed as-built | Fits into the Lower Cheek Plate | Y | Site | Tom | Y | Y | Tub 3 | WL-1-TUR-GVA | 4
Lower Bearing Housing | Component | O-27672 / O-60600 | N/A | Lower Guide Vane Bearing Housing | Lower Bearing Housing | 20 | New | See O-60590 for detailed drawing | Y | S&W | Matt | N/A |  | S&W | WL-1-TUR-GVA | 1
Lower Bearing Housing | Bearing | O-27672 / O-60600 | N/A | Lower Bearing Housing Bush | IDØ89 Deva.Tex | 20 | Will there be a new drawing for this? Are there spares? | No details listed on drawing | Y | S&W | Matt | N/A |  | Installed in Lower Bearing Housing | WL-1-TUR-GVA | 5
Lower Bearing Housing | Fastener | O-27715 | 15 | Lower Bearing Housing Bolts | M24 x 75mm, Hex Head Bolt, Z/P, Class 4.6 | 80 |  | Changed from Stud to Bolt | N | Site | Josh | Y |  | Tub 3 | WL-1-TUR-GVA | 0
Lower Bearing Housing | Fastener | O-27715 | 16 | Nut | Not required | 80 | Not required | Need to remove as studs to be changed to bolts? | Y | Site | Josh | N |  | N/A | WL-1-TUR-GVA | 0
Lower Bearing Housing | Tab Washer | O-27716 | 17 | Lower Bearing Housing Bolt Nordlocks | 24mm Nordlock Washer Z/P | 80 | Locking Tab replaced with Nordlock | Locking Tab to be replaced with Nordlock | Y | Site | Josh | Y |  | Tub 3 | WL-1-TUR-GVA | 0
Upper Bearing Housing | Component | O-27672 / O-60600 | N/A | Upper Bearing Housing | Upper Bearing Housing | 80 | New | See O-60613 for detailed drawing | Y | S&W | Matt | N/A |  | S@W | WL-1-TUR-GVA | 1
Upper Bearing Housing | Bearing | O-27672 / O-60600 | N/A | Upper Bearing Housing Bush | IDØ99 Deva.Tex | 40 | Will there be a new drawing for this? Are there spares? | Two bushes per Bearing Housing | Y | Voith | Matt | N/A |  | Installed in Upper Bearing Housing | WL-1-TUR-GVA | 10
Upper Bearing Housing | Fastener | O-27672 | N/A | Upper Bearing Housing Bolts | M20 x 90mm Hex Head Bolt, Class 4.6 Z/P | 140 |  | For securing of the the Upper Bearing Housing and Up Thrust Bearing | Y | Site | Josh | Y |  | Tub 4 | WL-1-TUR-GVA | 0
Upper Bearing Housing | Fastener | O-27672 | N/A | Upper Bearing Housing Studs | M20 x 110mm Long, Class 4.6 Z/P | 20 | Required for under Lever | One per Bearing Housing due to Lever design. | Y | Site | Josh | Y |  | Tub 4 | WL-1-TUR-GVA | 0
Upper Bearing Housing | Fastener | O-27672 | N/A | Upper Bearing Housing Nuts | M20 Z/P, Class 5 | 20 | To suit Upper Bearing Housing Studs | One per Bearing Housing due to Lever design. | Y | Site | Josh | Y |  | Tub 4 | WL-1-TUR-GVA | 0
Upper Bearing Housing | Component | O-25959 | 3 | Upper Thrust Bearing Holder | Upper Thurst Bearing Holder | 20 | Refurbished | O-60253 There are 2 halves to each Bearing | Y | Site | Josh | Y |  | Tub 4 | WL-1-TUR-GVA | 0
Upper Bearing Housing | Dowel | O-27672 | N/A | Upper Bearing Housing Dowels | M20 x 90mm Taper Dowel | 40 | Need more details so we can confirm site requirements? Dia enlarged from M20 original. Custom requied. | Supplied by Cambridge | Y | Cambridge | Matt | Y |  | Tub 4 | WL-1-TUR-GVA | 0
Upper Bearing Housing | Bearing | O-25959 | 4 | Upper Thurst Bearing Liner | Deva.Tex | 20 |  | O-60260 There are 2 halves to each Carbon Ring set and they are to be adhered to the Upper Thurst Bearing Holder | Y | S&W | Matt | Y |  | Installed in Thrust Bearing Holder Rings | WL-1-TUR-GVA | 4.5
Upper Bearing Housing | Seal | O-29370 / O-60600 | N/A | Seal for Upthrust Bearing | BS363 NBR70 O'Ring (164.47mm x 5.33mm) | 20 | Confirmed as-built |  | Y | Site | Tom | Y |  | Tub 4 | WL-1-TUR-GVA | 0
Upper Bearing Housing | Seal | O-27672 / O-60600 | N/A | Upper Bearing Housing Bottom Outer Seal | Vulcansied O'Ring 154mm ID x 6mm NBR70 | 20 | Confirmed as-built | Drawing is hard to determine size, no shore listed | Y | Site | Tom | N |  | Tub 4 | WL-1-TUR-GVA | 0
Upper Bearing Housing | Seal | O-27672/O-60600 | H514332 | Upper Bearing Housing Inner Seal | Hydraulic Rod Seal - PU, 99IDx130ODx15 | 20 |  | No details listed on drawing | Y | Site | Tom | N |  | Tub 4 | WL-1-TUR-GVA | 4
Upper Bearing Housing | Fastener | O-27672/O-60600 | H502353 | Upper Bearing Housing Inner Seal Retainer | Circlip (Retaining Ring, d1=135 acc. To DIN 472) | 20 |  | No details listed on drawing | Y | S&W | Matt | N/A |  | Tub 4 | WL-1-TUR-GVA | 30
Upper Bearing Housing | Component | O-27672/O-60600 | H534652 | Upper Bearing Housing Inner Seal Energiser | Steel Ring Energiser (Packing Support) | 20 |  | No details listed on drawing | Y | S&W | Matt | N/A |  | Tub 4 | WL-1-TUR-GVA | 5
Upper Bearing Housing | Component | O-27672/O-60600 | H534651 | Upper Bearing Housing Inner Seal Packing Support | Steel Ring (Packing Support) 130OD x 6thk | 20 | [8 empty] | WL-1-TUR-GVA | 6

## Bottom Ring
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Bottom Ring | Component | O-27715 | 1 | Bottom ring |  | 1 | Weight = ??kgs |  | Y | Firmins | Matt | N/A | Y | Installed | WL-1-TUR-COV | 0
Bottom Ring | Seal | O-27715 | 14 | Bottom Ring Oring | 7mm, 70 shore | 1 | Changed to smaller Oring ue to new groove design |  | Y | Site | Tom | Y | Y | Installed | WL-1-TUR-COV | 0
Bottom Ring | Fastener | O-27715 | 15 | Stud for Bottom Ring | M38 x 2mm Pitch, plain steel, 4140 | 32 | Supplied new from Voith |  | Y | Voith | Tom | Y | Y | Installed | WL-1-TUR-COV | 8
Bottom Ring | Fastener | O-27715 | 16 | Nut | M38 x 2mm Pitch, plain steel, 4140 | 32 | New ones made to suit Voith Studs |  | N | Site | Tom | Y | Y | Installed | WL-1-TUR-COV | 9
Bottom Ring | Fastener | O-27715 | N/A | Nordlock for Bottom Ring Stud | M39 Nordlock Washer, Z/P | 32 | previously not installed |  | Y | Voith | Tom | Y | Y | Bottom Cover Tub 1 | WL-1-TUR-COV | 0
Bottom Ring | Dowel | O-27715 | 17 | Dowel Pin for Bottom Ring | 20 x 120 | 4 | Need to make new once Cover installed | Changed to parallel | N | Site | Kodi | Y | Y | Bottom Cover Tub 1 | WL-1-TUR-COV | 0
Bottom Ring | Fastener | O-27715 | 18 | Grub Screw for Dowel Pin | M16 x 30mm | 4 | Changed to grub screw for female hole in dowel |  | N | Site | Kodi | N | N | Bottom Cover Tub 1 | WL-1-TUR-COV | 0
Bottom Ring | Fastener | O-27715 | 19 | Washer for Taper Pin | M16 | 4 | Redundant |  | N | Site | Kodi | N | N | N/A | WL-1-TUR-COV | 0
Bottom Ring | Fastener |  | N/A | Nut Cover | Nylon nut cover | 32 | [8 empty] | WL-1-TUR-COV | 5

## Top Cover
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
uc
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Top cover | Component | O-27712 | 1 | Top Cover |  | 1 | Weight = ??kgs |  | Y | Firmins | Matt | N/A | Y | Installed | WL-1-TUR-COV | 0
Top cover | Fastener | O-27712 | 27 | Stud | M38 x 2mm Pitch, plain steel, 4140 | 32 | Supplied new from Voith |  | Y | Voith | Matt | Y | Y | Installed | WL-1-TUR-COV | 8
Top cover | Fastener | O-27712 | 28 | Nut | M38 x 2mm Pitch, plain steel, 4140 | 32 | New ones made to suit Voith Studs |  | Y | Site | Tom | Y | Y | Installed | WL-1-TUR-COV | 9
Bottom Ring | Fastener | O-27715 | N/A | Nordlock for Top Cover Stud | M39 Nordlock Washer, Z/P | 32 | Previously not installed |  | Y | Voith | Tom | Y | Y | Top Cover Tub 1 | WL-1-TUR-COV | 0
Top cover | Seal | O-27712 | 29 | Round rubber packing | 9mm, 70 Shore | 1 |  |  | N | Site | Tom | Y | Y | Top Cover Tub 1 | WL-1-TUR-COV | 0
Top cover | Seal | O-27712 | 30 | Round rubber packing | 10mm, Shore | 1 |  |  | N | Site | Tom | Y | Y | Top Cover Tub 1 | WL-1-TUR-COV | 0
Top cover | Dowel | O-27712 | 34 | Dowel Pin for Top Cover | 20 x 120 | 4 | Need to make new once Cover installed | Changed to parallel | N | Site | Kodi | Y | Y | Top Cover Tub 1 | WL-1-TUR-COV | 0
Top cover | Fastener | O-27712 | 35 | Grub Screw for Dowel Pin | M16 x 30mm | 4 | Changed to grub screw for female hole in dowel |  | Y | Site | Kodi | N | N ? | Top Cover Tub 1 | WL-1-TUR-COV | 0
Top cover | Fastener | O-27712 | 36 | Flat Washer | M16, plain steel | 4 | Redundant |  | Y | Site | Kodi | N | N | N/A | WL-1-TUR-COV | 0
Top Cover | Fastener |  | N/A | Nut Cover | Nylon nut cover | 32 | [8 empty] | WL-1-TUR-COV | 5

## Upper Guide & Thrust Bearing
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | Comments | General Information | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Bearing shell | Component | O-27136-002 | 2 | Bearing Shell Segment | Segment type 2 | 3 |  | Assembled with items 1 and 3 Approx 47kgs per segment | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-THG-GB1 | 0
Bearing shell | Component | O-27136-002 | 6 | Bearing Shell Splash Ring Half | Upstream Half | 1 |  |  | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-THG-GB1 | 0
Bearing shell | Component | O-27136-002 | 7 | Bearing Shell Splash Ring Half | Loading Bay Half | 1 |  |  | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-THG-GB1 | 0
Inner oil pot cover | Component | O-26759-002 | 5 | Threaded plug | For plugging ports in Labyrinth Groove | 12 |  | Installed in item 2 | Y | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Inner oil pot cover | Component | O-26759-002 | 6 | Labyrinth Groove Parallel pin | 3 x 24 | 12 |  | Installed in item 2 | Y | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Bearing shell | Fastener | O-27136-002 | 10 | Grub screw for setting oil flow | M12 X 25, Plain Steel | 12 | Need to confirm details? | Screwed into Bearing segment to assist with setting oil flow | Y | Cambridge | Matt | N | Y | Cambridge | WL-1-ALT-THG-GB1 | 0
Bearing shell | Fastener | O-27136-002 | 12 | Hex screw for Splash Ring | M10 X 20mm, plain steel class 5.6 | 24 | Confirm Details with Hally? |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-THG | 0
Bearing shell | Tab Washer | O-27136-002 | 13 | Nordlock Washer for Splash Ring Screw | 10mm Nordlock Washer, S/S | 24 | Changed to Nordlock | For item 12, Chanded to Nordlock | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-THG | 0
Inner oil pot cover | Component | O-26759-002 | 10 | Air balance measuring point | M8? | 1 |  | Installed in item 2 | Y | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Bearing shell | Fastener | O-27136-002 | 15 | Hex screw for Bearing Segment | M20 x 70mm, plain steel class 5.6 | 12 | Confirm Details? No longer at site? |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-THG | 0
Bearing shell | Nordlock | O-27136-002 | 16 | Nordlock Washer for Bearing Segment Screw | 20mm, Nordlock Washer, S/S | 12 |  | For item 15, | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-THG | 0
Bearing shell | Dowel | O-27136-003 | 18 | Taper Pin for Bearing Segment | 16mm x 100mm | 6 | Confirm Details of new arrangement? No longer at site? |  | Y | Cambridge | Matt | N/A | N | Tub 1 | WL-1-ALT-THG | 0
Outer oil pot cover | Component | O-27008-002 | 4 | Reinforcement for Lifting Point | M16 | 4 |  | Welded to Item with M16 hole tapped for lifting | Y | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Bearing shell | Dowel | O-27136-003 | 19 | Nut for Bearing Segment Taper Pin | M16 | 1 |  | For item 18 | N | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Bearing shell | Dowel | O-27136-003 | 20 | Washer for Bearing Segment Taper Pin | M16 | 1 |  | For item 18 | N | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Bearing shell | Seal | O-27136-003 | 21 | Rubber for Sealing Bearing Segments | 12 x 65, 95 nitr | 12 |  | 2 pieces between each segment, glued in place | N | Cambridge | Matt | N | N | Tub 1 | WL-1-ALT-THG-GB1 | 9
Bearing shell | Component | O-27136-003 | 22 | Plate for Bearing Segment Oil Groove - Left Hand | Copper Plate | 6 |  | Bolted to Bearing Segment and 0.20mm below white metal | Y | Cambridge | Matt | N/A | Y | Installed on Bearing | WL-1-ALT-THG | 0
Bearing shell | Component | O-27136-003 | 23 | Plate for Bearing Segment Oil Groove - Right Site Hand | Copper Plate | 6 |  | Bolted to Bearing Segment and 0.20mm below white metal | Y | Cambridge | Matt | N/A | Y | Installed on Bearing | WL-1-ALT-THG | 0
Bearing shell | Fastener | O-27136-003 | 24 | Countersunk Flat Head screw Oil Groove Plate | M8 x 15mm, plain steel | 48 | Confirm Details? Screws no longer at site? | Secure with Loctite and centre pop | N | Cambridge | Matt | N | Y | Installed on Bearing | WL-1-ALT-THG | 0
Cool Oil Pipes | Component | O-27633 | 16 | Cool Oil Pipe | Cool Oil Pipe | 12 |  | Consists of item 29, 42, 44, 45, 46 and 49 | Y | Cambridge | Matt | N/A | Y | Loading Bay | WL-1-ALT-THG | 0
Cool Oil Pipes | Fastener | O-27633 | 56 | Hex Screw for Cool Oil Pipe Clamp | M10 X 20mm, plain steel class 5.6 | 12 | Confirm Details? |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG | 0
Cool Oil Pipes | Nordlock | O-27633 | 59 | Nordlock Washer for Hex Screw | 10mm Nordlock Washer, S/S | 12 |  | For item 56 | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG | 0
Cool Oil Pipes | Fastener | O-27633 | 55 | Hex Screw for Cool Oil Pipe | M12 X 30mm, plain steel class 5.6 | 48 | Confirm Details? |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG | 0
Cool Oil Pipes | Nordlock | O-27633 | 58 | Nordlock Washer for Hex Screw | 12mm Nordlock Washer, S/S | 48 |  | For item 55 | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG | 0
Inner oil pot cover | Component | O-26759-002 | 1 | Inner Oil Pot Cover - Top | Cover with Labyrinth | 1 |  |  | Y | Cambridge | Matt | N/A | Y | Loading Bay | WL-1-ALT-THG | 0
Inner oil pot cover | Component | O-26759-002 | 2 | Inner Oil Pot Cover - Bottom | Lower Labyrinth Section | 1 |  | Bolted to Thrust Block | Y | Cambridge | Matt | N/A | Y | Loading Bay | WL-1-ALT-THG | 0
Inner oil pot cover | Fastener | O-26759-002 | 7 | Capscrew for Inner Oil Pot Cover - Bottom | M10 x 20mm, Z/P, class 12.9 | 24 |  |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-THG | 0
Inner oil pot cover | Fastener | O-26759-002 | N/A | Nordlock Washer for Inner Oil Pot Cover - Bottom Capscrews | 10mm Nordlock Washer, Z/P | 24 | For item 7 | For item 7 | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-THG | 0
Inner oil pot cover | Fastener | O-26759-002 | 8 | Hex bolt for Inner Oil Pot Cover - Top | M12 x 25mm, Z/P, class 5.6 | 36 | Bolts no longer at site? |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-THG | 0
Inner oil pot cover | Nordlock | O-26759-002 | 9 | Nordlock Washer for Inner Oil Pot Cover bolts | 12mm Nordlock Washer, Z/P | 60 |  | For item 7 and 8 | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-THG | 0
Inner oil pot cover | Seal | O-27089 | 17 | O-ring for Inner Oil Pot Cover - Bottom | 8mm Oring, 70 Shore | 1 |  |  | N | Site | Tom | N | N | Tub 3 | WL-1-ALT-THG | 0
Inner oil pot cover | Seal | O-26995 | 35 | Inner Oil Pot Cover Oring | 8mm Oring, 70 Shore | 1 |  |  | N | Site | Tom | N | Y | Tub 3 | WL-1-ALT-THG | 0
Lower Spring Plate | Component | O-26995 | 22 | Keeper Plate for Bottom Spring Plates | Keeper Plate | 12 |  |  | Y | Cambridge | Matt | N/A | Y | Tub 2 | WL-1-ALT-THG | 0
Lower Spring Plate | Tab Washer | O-26995 | 23 | Double Locking Plate for Hex Screw | 2 x 14mm holes, 50mm centres | 12 |  | for item 29 | Y | Site | Pat | N | Y | Tub 2 | WL-1-ALT-THG | 0
Lower Spring Plate | Fastener | O-26995 | 29 | Hex Screw for Keeper Plate | M12 X 25mm, plain steel class 5.6 | 24 |  | For item 22 | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG | 0
Lower Spring Plate | Dowel | O-26995 | 30 | Locating Pin | 13mm (H8) x 20mm Din 7 | 12 | Confirm with Hally? | For item 22 | N | Site | Jeremy | N | Y | Tub 2 | WL-1-ALT-THG | 0
Oil Injection | Component | O-27608 | 19 | Clamps for Oil Injection Ringmain | Pipe Clamp, Din 1592 | 13 |  |  | Y | Cambridge | Matt | N/A | Y | Installed in Bracket, Changed Design | WL-1-ALT-THG | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 1 | Thrust bracket |  |  |  |  | N/A |  |  |  |  | N/A | WL-1-ALT-THG | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 2 | Oil Stabiliser |  |  |  |  | N/A |  |  |  |  | N/A | WL-1-ALT-THG-THR | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 3 | Upper spring plate |  |  |  | These spares are at Cambridge? | N/A |  |  |  |  | N/A | WL-1-ALT-THG-THR | 12 TBC (Cambridge) | Already in System?
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 4 | Lower spring plate |  |  |  | These spares are at Cambridge? | N/A |  |  |  |  | N/A | WL-1-ALT-THG-THR | 12 TBC (Cambridge) | Already in System?
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 5 | Thrust pads |  |  |  | item 2 on drawing O-26349 | N/A |  |  |  |  | N/A | WL-1-ALT-THG-THR | 12 TBC (Cambridge) | Already in System?
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 6 | Upper Guide Bearing shell |  |  |  | Type 2 on drawing O-27136 | N/A |  |  |  |  | N/A | WL-1-ALT-THG-GB1 | 1 (Cambridge) | Already in System?
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 7 | Thrust block & runner |  |  |  |  | N/A |  |  |  |  | N/A | WL-1-ALT-THG | 1(Cambridge)
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 8 | Inner oil pot cover |  |  |  | item 1 and 2 on drawing O-26759 | N/A |  |  |  |  | N/A | WL-1-ALT-THG | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 9 | Outer oil pot cover |  |  |  | item 1 on drawing O-27008 | N/A |  |  |  |  | N/A | WL-1-ALT-THG | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 10 | Exciter support |  |  |  | item 1 on drawing O-27292 | N/A |  |  |  |  | N/A | WL-1-ALT-THG | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 11 | Cooling equipment |  |  |  |  | N/A |  |  |  |  | N/A | WL-1-ALT-THG-HTX | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 12 | Clamping device |  |  |  |  | N/A |  |  |  |  | N/A | WL-1-ALT-THG | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 13 | Stopper |  |  |  |  | N/A |  |  |  |  | N/A | WL-1-ALT-THG | 0
Thrust and Guide Bearing Assembly | Component | O-27638-001 | 14 | Stopper |  |  |  |  | N/A |  |  |  |  | N/A | WL-1-ALT-THG | 0
Oil Injection | Fastener | O-27608 | 23 | Hex Screw for Clamps | M10 X 15mm, plain steel class 5.6 | 13 | Confirm Grade | For item 19 | Y | Site | Josh | Y | Y | Installed in Bracket, Changed Design | WL-1-ALT-THG | 0
Oil Injection | Nordlock | O-27608 | 28 | NordlockWasher for Hex Screw | 10mm Nordlock Washer, S/S | 13 |  | For item 19 | Y | Site | Josh | Y | Y | Installed in Bracket, Changed Design | WL-1-ALT-THG | 0
Outer oil pot cover | Component | O-27008-002 | 1 | Outer Oil Pot Cover |  | 1 | Need details of Oring? |  | Y | Cambridge | Matt | N/A | Y | Loading Bay | WL-1-ALT-THG | 0
Outer oil pot cover | Component | O-27008-002 | 6 | Outer Oil Pot Cover Inspection Cover | Inspection Cover Assembly (Including Seals) | 4 | Need details of Bolts and Seals? |  | Y | Cambridge | Matt | N/A | N | ? | WL-1-ALT-THG | 0
Outer oil pot cover | Fastener | O-27008-002 | 7 | Hex Screw for Outer Oil Pot Cover | M12 X 25mm, Z/P, class 5.6 | 112 | Confirm Details? Bolts no longer at site? |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-THG | 0
Outer oil pot cover | Nordlock | O-27008-002 | 8 | Nordlock Washer for Outer Oil Pot Cover screw | 12mm Nordlock Washer, Z/P | 112 | Confirm Details? No longer at site? | For item 7 | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-THG | 0
Outer oil pot cover | Component | O-27008-002 | 10 | Flange | ? | 1 | Need details of Bolts and Seals? |  | N | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Outer oil pot cover | Seal | O-26995 | 36 | Outer Oil Pot Cover Inner Oring | 8mm Oring, 70 Shore | 1 |  |  | N | Site | Tom | N | Y | Tub 3 | WL-1-ALT-THG | 0
Outer oil pot cover | Seal | O-26995 | 37 | Outer Oil Pot Cover Outer Oring | 8mm Oring, 70 Shore | 1 |  |  | N | Site | Tom | N | Y | Tub 3 | WL-1-ALT-THG | 0
Thrust and Guide Bearing Assembly | Component | O-27638-016 | 15/A | Outer Guide Bolt for Thrust Pad | Outer Guide Bolt for Thrust Pad | 12 |  |  | Y | Cambridge | Matt | N/A | Y | Tub 2 | WL-1-ALT-THG-THR | 0
Thrust and Guide Bearing Assembly | Component | O-27638-016 | 15/B | Inner Guide Bolt for Thrust Pad | Inner Guide Bolt for Thrust Pad | 12 |  |  | Y | Cambridge | Matt | N/A | Y | Tub 2 | WL-1-ALT-THG-THR | 0
Thrust and Guide Bearing Assembly | Component | O-27638-017 | 16 | Pressure oil injection | Ringmain and Pigtail assembly | 1 | Confirm new arrangment supplied by Workshop? |  | Y | Cambridge | Matt | N/A | Y | installed in Thrust Bracket | WL-1-ALT-THG-THR | 0
Thrust Brg Pads | Component | O-27490 | 4 | Thrust pads | Type 2 as per drawing | 12 |  | There are three drilling patterns for the Bearings See items 1, 2 and 3 | Y | Cambridge | Matt | N/A | Y | Loading Bay | WL-1-ALT-THG-THR | 0
Thrust Brg Pads | Component | O-27490 | 9 | Stripping Blade | Oil Scrapper | 12 |  | Fitted to the side of the Thrust Pad. TO be set level with white metal | Y | Cambridge | Matt | N/A | Y | Installed on Thrust pad | WL-1-ALT-THG-THR | 0
Thrust Brg Pads | Fastener | O-27490 | 10 | Flat Head Slotted Screw for Stripping Blade | M8 x 12, Plain Steel | 48 | Confirm Details? Bolts no longer at site? | For item 9 | Y | Cambridge | Matt | N | Y | Installed on Thrust pad | WL-1-ALT-THG-THR | 0
Upper Spring Plate | Component | O-27490 | 6 | Ring for Upper Spring Plate | Support Ring for Upper Spring Plate | 12 |  | Used to secure the Upper Spring Plate to the Thrust Pad | Y | Cambridge | Matt | N/A | Y | Tub 2 | WL-1-ALT-THG-THR | 12 | Already in System?
Upper Spring Plate | Fastener | O-27490 | 7 | Capscrew for Upper Spring Plate Ring | M8 x 15mm, plain steel Class 12.9 | 48 | Confirm Details? | For item 6 | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG-THR | 0
Upper Spring Plate | Nordlock | O-27490 | 8 | Nordlock Washer for Cap Screw | 8mm Nordlock Washer, S/S | 48 |  | For item 7 | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG-THR | 0
Warm Oil Pipes | Component | O-27633 | 17 | Warm Oil Pipe | Warm Oil Pipe StraigSite Section | 6 |  | Consists of item 31, 32 and 1 x 48 | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-THG | 0
Warm Oil Pipes | Component | O-27633 | 18 | Elbow for Warm Oil Pipe | Warm Oil Pipe Elbow Section | 6 |  | Consists of item 33, 34, 40 and 47 | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-THG | 0
Warm Oil Pipes | Component | O-27633 | 31 | Short Pipe section for Warm Oil Pipe assembly | 1 1/4" OD Pipe, 1 1/4" BSP Thread (either end), 130mm Long | 6 |  | Assembled as part of item 17 | Y | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Warm Oil Pipes | Component | O-27633 | 32 | Long Pipe section for Warm Oil Pipe assembly | 1 1/4" OD Pipe, 1 1/4" BSP Thread (either end), 260mm Long | 6 |  | Assembled as part of item 17 | Y | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Warm Oil Pipes | Component | O-27633 | 32 | Long Pipe section for Warm Oil Pipe assembly | 1 1/4" BSP Barrel Union | 12 |  | 2 per assembly. Assembled as part of items 17 and 18 | Y | Cambridge | Matt | N/A |  | N/A | WL-1-ALT-THG | 0
Warm Oil Pipes | Fastener | O-27633 | 55 | Hex Screw for warm Oil Pipe | M12 X 30mm, plain steel class 5.6 | 24 | Confirm Details? |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-THG | 0
Warm Oil Pipes | Nordlock | O-27633 | 58 | Nordlock Washer for Hex Screw | 12mm Nordlock Washer, S/S | 24 |  | For item 55 | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-THG | 0
Oil Ring | Nordlock | O-26995 | 25 | Nordlock for Oil Ring Screw | 16mm Nordlock Washer, S/S | 144 | For item 28 |  | Y | Site | Josh | Y | Y | Installed | WL-1-ALT-THG | 0
Oil Ring | Fastener | O-26995 | 28 | Hex Screw for Oil Ring | M16 X 60mm, plain steel class 5.6 | 144 |  |  | Y | Site | Josh | Y | Y | Installed | WL-1-ALT-THG | 0

## Thrust Bracket
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Thrust Bracket | Component | O-59796-001 | 1 | Shim for Thrust Bracket | Various Thickness' | 1 | For shimming the Thrust Bracket to correct level |  | Y | Andritz | Tom | N/A | Y | Inward Goods Store | WL-1-ALT-THG | 1
Thrust Bracket | Fastener | O-59796-001 | 2 | Hex Bolts for Thrust Bracket | M42 x 120mm, Z/P class 8.8 | 8 |  |  | Y | Andritz | Josh | N/A | Y | Tub 1 | WL-1-ALT-THG | 0
Thrust Bracket | Nordlock | O-59796-001 | 3 | Nordlock for Thrust Bracket Bolts | M42 Nordlock Washer, Z/P | 8 | For item 2 |  | Y | Andritz | Josh | N/A | Y | Tub 1 | WL-1-ALT-THG | 0
Thrust Bracket | Dowel | O26995 | 4 | Dowel Pin for Thrust Bracket | 30mm x 120 | 8 | TO be machined to suit after dowelling of the Thrust Bracket |  | N | Andritz | Jeremy | Y | Y ? | Tub 1 | WL-1-ALT-THG | 0
Thrust Bracket | Dowel | O26995 | 33 | Nut for Taper Pin | M24 | 8 |  | Likely new with Andritz design, Need to confirm? | Y | Andritz | Josh | N/A |  | N/A | WL-1-ALT-THG | 0
Thrust Bracket | Component | O-26276 | 1 | Labyrinth Ring and Gland | Labyrinth Ring and Gland | 1 | Includes item 2 | ? | Y | Site | Jeremy | N/A | Y | Loading Bay | WL-1-ALT-THG | 0
Thrust Bracket | Fastener | O-26276 | 3 | Hex Bolt for Labyrinth Ring | M12 x 30mm, Z/P, class 5.6 | 12 |  |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG | 0
Thrust Bracket | Fastener | O-26276 | 4 | Hex Bolt for Labyrinth RIng Jacking Bolt Hole | M12 x 15mm, Z/P, class 5.6 | 3 | Screws into jacking bolt hole to help support locking plate that is used to secure item 7 |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG | 0
Thrust Bracket | Tab Washer | O-26276 | 5 | Double Locking Plate | 2 x 14mm holes, 50mm centres | 3 | Used With item 3 and 4 to secure item 7 |  | Y | Site | Pat | N | N | Tub 2 | WL-1-ALT-THG | 0
Thrust Bracket | Nordlock | O-26276 | 6 | Nordlock for Labyrinth Ring Bolt | 12mm Nordlock Washer, Z/P | 9 | For item 3 |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-ALT-THG | 0
Thrust Bracket | Dowel | O-26276 | 7 | Straight Pin for Labyrinth Ring | 10(H8) x 28mm Din 7 | 3 | For item 1 |  | Y | Site | Jeremy | N | N ? | Tub 2 | WL-1-ALT-THG | 0
Stator | Fastener | O-59724-002 | 15 | Hex Bolts for Thrust Bracket Sole Plate | M30 x 80mm, Z/P class 8.8 | 8 |  |  | Y | Andritz | Josh | N/A | Y | Tub 1 | WL-1-ALT-THG | 0
Stator | Nordlock | O-59724-002 | 16 | Nordlock for Thrust Bracket Sole Plate Bolts | M30 Nordlock Washer, Z/P | 8 |  |  | Y | Andritz | Josh | N/A | Y | Tub 1 | WL-1-ALT-THG | 0
Stator | Dowel | O-59724-002 | 17 | Dowel Pin for Thrust Bracket Sole Plate | 30mm x 85 | 8 |  |  | Y | Andritz | Josh | N/A | Y | Tub 1 | WL-1-ALT-THG | 0

## Thrust Block
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Inforamtion | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Shaft | Component |  | N/A | Thrust Block Locating Key | ? |  | Fits in Shaft to locate Thrust Block | ? | N | Cambridge | Jeremy/Tom |  |  | Loading Bay | WL-1-ALT-SHT | 0
Shaft | Fastener | O-27087 | N/A | Caphead Screw for Thrust Block Key | M12 x 30mm, Capscrew, Plain Steel | 2 | Noted on drawing O-27087 | Need to confirm if these are at Saunders or Cambridge? | Y | Site | Josh | Y | Y | Thrust Block Tub 1 | WL-1-ALT-THG | 0
Shaft | Nordlock |  | N/A | Lock washer for Caphead Screw for Thrust Block Key | 12mm Nordlock Washer, Z/P | 2 |  | Need to confirm if this bolt had one or if it needs one? | Y | Site | Josh | Y | Y | Thrust Block Tub 1 | WL-1-ALT-THG | 0
C-Keys | Component | O-27089 | 5 | Thrust Ring | Splits in two, known as C-Keys | 1 |  |  | Y | Cambridge | Matt | N/A | Y | Loading Bay | WL-1-ALT-THG | 1 (Cambridge)
C-Keys | Component | O-27089 | 6 | Lock Ring for Thrust Ring | Keeper for the C-Keys | 1 |  |  | Y | Cambridge | Matt | N/A | Y | Operating Floor | WL-1-ALT-THG | 1 (Cambridge)
C-Keys | Fastener | O-27089 | 14 | Hex Screw for Thrust Ring (C-Keys) | M16 x 50mm, Z/P, Class 5.6 | 8 |  |  | Y | Site | Josh | Y | Y | Thrust Block Tub 1 | WL-1-ALT-THG | 0
C-Keys | Tab Washer | O-27089 | 15 | Tab Washer for Thrust Ring Screws | 16mm Din 93 | 8 |  |  | Y | Site | Josh | Y | Y | Thrust Block Tub 1 | WL-1-ALT-THG | 0

## Lower Guide Bearing
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-28
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
LGB Oil Pot | Component | O-27010-002 | 1 | Oil Pot - Upstream Half |  | 1 |  |  | Y | Cambridge | Matt | N/A | Y | Cethana | WL-1-ALT-GB1 | 0
LGB Oil Pot | Component | O-27010-002 | 2 | Oil Pot - Loading Bay Half |  | 1 |  |  | Y | Cambridge | Matt | N/A | Y | Cethana | WL-1-ALT-GB1 | 0
LGB Oil Pot | Component | O-27010-002 | 16 | Fitted Bolt (Barrel Bolt) for Oil Pot Joint | M12 X 60mm, plain steel, class 4.8 | 4 | Hole 13mm H7 |  | Y | Cambridge | Matt | N/A | Y | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Fastener | O-27010-002 | 17 | Hex screw for Oil Pot Joint | M12 X 70mm, Z/P, class 5.6 | 38 |  |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Fastener | O-27010-003 | 18 | Hex Screw for Oil Pot | M12 X 50mm, Z/P, class 5.6 | 48 |  |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Fastener | O-27010-003 | 19 | Countersunk head screw | M8 x 15mm, | 24 |  |  | Y | Site | Josh | Y | N | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Component | O-27010-003 | 20 | Plug for drain valve | 1" | 2 | For item 29 | Replace? | Y | Site | Josh | N | N | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Fastener | O-27010-003 | 21 | Hexagon nut for Oil Pot hex screw | M12, Z/P, class 5.6 | 42 | for items 16 and 17 |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Tab Washer | O-27010-003 | 22 | Double locking tab for Oil Pot Joint | 14mm hole with 45mm centres | 10 | For item 16 and 17 |  | N | Site | Josh | Y | N | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Tab Washer | O-27010-003 | 23 | Double locking plate | 14mm hole with 50mm centres | 10 | For item 17 |  | N | Site | Josh | Y | N | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Nordlock | O-27010-003 | 24 | Nordlock Washer for Hex Screw | 12mm Nordock Washer Z/P | 48 | For item 18 |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Component | O-27010-003 | 25 | Drain Valve Seal ring | Copper? | 2 | For item 29 | Replace? | Y | Site | Tom | N | N | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Seal | O-27010-003 | 26 | Gasket for Oil Pot Joint | 1mm Gasket paper | 2 |  | Confirm Material Required? | Y | Site | Tom | N | N | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Seal | O-27010-003 | 27 | Oring for Oil Pot to Lower Bracket | 8mm, 70 Shore | 1 | Groove = ID 1375, OD 1400 | Need to confirm shore hardness? | Y | Site | Tom | N | N | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Component | O-27010-003 | 28 | 1" Nipple for Drain Valve | 1" | 2 | For item 29 | Replace? | Y | Site | Josh | N | N | Tub 2 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Component | O-27010-003 | 29 | Oil Pot Drain Valve | 1" Valve | 2 |  | Replace? | Y | Site | Josh | N | N | Tub 2 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Tab Washer | O-27010-003 | 31 | Double locking plate | 14mm hole with 70mm centres | 2 | For item 17 |  | Y | Site | Josh | Y | N | Tub 1 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Component | O-27010-003 | 33 | Shaft Current Device Brush Holder - Threaded section | M16 Thread | 1 |  | Is this still needed? | Y | Site | Tom | N/A | N | Tub 2 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Component | O-27010-003 | 34 | Shaft Current Device Brush Holder - Threaded section | Rod Section | 1 |  | Is this still needed? | Y | Site | Tom | N/A | N | Tub 2 | WL-1-ALT-GB1 | 0
LGB Oil Pot | Component | O-27010-003 | 35 | Toothed washer for Shaft Current Device Threaded section | M16 toothed washer | 1 |  | Just use loctite? | N | Site | Tom | N/A | N | Tub 2 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Component | O-27012-1 | 2 | Upper Labyrinth Ring |  | 1 | two halves |  | Y | Cambridge | Matt | N/A | Y | Gowrie Park | WL-1-ALT-GB1 | 0
LGB Labyrinth | Nordlock | O-27012-1 | 8 | Nordlock for Upper Labyrinth Ring screw | 10mm Nordlock Washer Z/P | 32 |  |  | N | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Nordlock | O-27012-1 | 8 | Nordlock for Lower Labyrinth Ring screw | 10mm Nordlock Washer Z/P | 20 |  |  | N | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Fastener | O-27012-1 | 9 | Hex screw for Upper Labyrinth Ring | M10 X 25mm, Z/P, class 5.6 | 32 |  |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Fastener | O-27012-1 | 9 | Hex screw for Lower Labyrinth Ring | M10 X 25mm, Z/P, class 5.6 | 20 |  |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Seal | O-27012-1 | 10 | Gasket for Upper Labyrinth joint | 1mm Gasket paper | 2 |  | Confirm Material Required? | Y | Site | Tom | N | N | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Fastener | O-27012-1 | 11 | Hex screw for Upper Labyrinth joint | M12 X 75mm, Z/P, class 5.6 | 2 | For item 2 |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Component | O-27012-1 | 12 | Fitted bolt (Barrel Bolt) for Upper Labyrinth joint | M12 X 60mm, plain steel, class 5.6 | 4 | For item 2 |  | Y | Cambridge | Matt | N/A | N | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Fastener | O-27012-1 | 13 | Nut for Upper Labyrinth joint | M12, Z/P, class 5.6 | 6 | For item 11 and 12 |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Nordlock | O-27012-1 | 14 | Nordlock for Upper Labyrinth joint | 12mm Nordock Washer Z/P | 24 | For item 11, 12 and 13 |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Component | O-27012-1 | 19 | Fitted bolt (Barrel Bolt) for Lower Labyrinth joint | M16 X 120mm, plain steel, class 4.8 | 2 | For item 24 |  | Y | Cambridge | Matt | N/A | N | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Fastener | O-27012-1 | 20 | Hex screw for Lower Labyrinth joint | M16 X 130mm, plain steel, class 5.6 | 2 | For item 24 |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Fastener | O-27012-1 | 21 | Nut for Lower Labyrinth joint | M16, plain steel, Class 5.6 | 4 | For item 19 and 20 |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Fastener | O-27012-1 | 22 | Flat washer for Lower Labyrinth joint | M16, plain steel, Class 5.6 | 8 | For item 19, 20 and 21 |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Tab Washer | O-27012-1 | 23 | Locking Tab Lower Labyrinth Ring joint | 18mm hole with 53mm centres | 8 | For item 19, 20 and 21 | Confirm size and dimensions | N | Site | Josh | Y | N | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Component | O-27012-1 | 24 | Lower Labyrinth Ring | Lower Labyrinth Ring | 2 |  |  | Y | Cambridge | Matt | N/A | Y | ? | WL-1-ALT-GB1 | 0
LGB Labyrinth | Seal | O-27012-1 | 25 | Gasket for Lower Labyrinth joint | 1mm Gasket paper | 2 |  | Confirm? | Y | Site | Tom | N | N ? | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Seal | O-27609 | 6 | Oring for Upper Labyrinth Ring | 8mm, 70 Shore | 1 |  | Confirm Shore and Size? | Y | Site | Tom | N | N ? | Tub 3 | WL-1-ALT-GB1 | 0
LGB Labyrinth | Seal | O-27087 | N/A | Oring for Lower Labyrinth Ring | 8mm, 70 Shore | 1 |  | Confirm Shore and Size? | Y | Site | Tom | N | N ? | Tub 3 | WL-1-ALT-GB1 | 0
LGB Seal Air | Component | O-27635 | 1 | Seal Air Pipework for Labyrinth | Seal Air Pipework for Upper Labyrinth | 1 |  |  | N | Cambridge | Matt | N/A | N | Tub 4 | WL-1-ALT-GB1 | 0
LGB Seal Air | Component | O-27635 | 2 | Seal Air Pipework for Oil Pot | Seal Air Pipework for LGB Oil Pot | 1 |  |  | N | Cambridge | Matt | N/A | N | Tub 4 | WL-1-ALT-GB1 | 0
LGB Seal Air | Seal | O-27635 | 12 | Gasket for Seal Air Pipework | 2mm Thick | 3 | For item 1 and 2 | Confirm Material Required? | N | Site | Tom | N | N ? | Tub 4 | WL-1-ALT-GB1 | 0
LGB Seal Air | Fastener | O-27635 | 14 | Hex Bolt for Seal Air Pipework | M10 X 35mm, Z/P, class 5.6 | 6 | For item 1 and 2 |  | Y | Site | Josh | Y | Y | Tub 4 | WL-1-ALT-GB1 | 0
LGB Seal Air | Nordlock | O-27635 | N/A | Nordlock Washer for Hex Screw | M10 Nordlock Washer, Z/P | 6 | For item 14 |  | Y | Site | Josh | Y | Y | Tub 4 | WL-1-ALT-GB1 | 0
Splash Cover | Component | O-26275 | 1 | Splash Cover | Two Halves | 2 | Approx total weight is 37.3kg's |  | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-GB1 | 0
Splash Cover | Fastener | O-26275 | 4 | Hex Screw for Splash Cover | M10 X 35mm, plain steel, class 5.6 | 12 |  |  | Y | Site | Josh | Y | Y | Tub 5 | WL-1-ALT-GB1 | 0
Splash Cover | Nordlock | O-26275 | 5 | Nordlock for Hex Screw | 10mm Nordlock Washer S/S | 12 |  |  | N | Site | Josh | Y | Y | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Component | O-26341 | 1 | Bearing Half | US Half? | 1 |  |  | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-GB1 | 1
LGB | Component | O-26341 | 2 | Bearing Half | LB Half? | 1 |  |  | Y | Cambridge | Matt | N/A | N | Cambridge | WL-1-ALT-GB1 | 1
LGB | Dowel | O-26341 | 12 | Taper Pin for Bearing | 20mm x 120mm | 2 | To be drilled and reamed on Bearing install |  | Y | Site | Josh | Y | N ? | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Tab Washer | O-26341 | 13 | Locking Plate | 10mm holes with 60mm centres | 2 |  |  | Y | Site | Josh | Y | N | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Fastener | O-26341 | 14 | Hex Screw | M8 x 12mm, plain steel, class 8.8 | 4 |  |  | Y | Site | Josh | Y | Y | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Nordlock | O-26341 | N/A | Nordlock Washer for Hex Screw | 8mm Nordlock Washer, S/S | 4 | For item 14 |  | Y | Site | Josh | Y | Y | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Fastener | O-26341 | 15 | Hex Screw | M24 x 80mm, plain steel, class 5.6 | 12 |  |  | Y | Site | Josh | Y | Y | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Nordlock | O-26341 | 16 | Nordlock for Hex Screw | 24mm Nordlock Washer S/S | 12 |  |  | Y | Site | Josh | Y | Y | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Fastener | O-26341 | 17 | Fitted bolt for LGB joint | M30 x 130mm, plain steel, class 5.6 | 2 |  | Supplied with Bearing | Y | Cambridge | Matt | N/A | N | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Fastener | O-26341 | 18 | Hex Screw for LGB Joint | M30 x 130mm, plain steel, class 5.6 | 2 |  | Supplied with Bearing | Y | Cambridge | Matt | N/A | N | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Fastener | O-26341 | 19 | Nut for LGB joint bolts | M30, plain steel, Class 5.6 | 4 |  | Supplied with Bearing | Y | Cambridge | Matt | N/A | N | Tub 5 | WL-1-ALT-GB1 | 0
LGB | Nordlock | O-26341 | 20 | Nordlock for LGB bolts | 30mm NordlockWasher, S/S | 8 |  | Supplied with Bearing | Y | Cambridge | Matt | N/A | N | Tub 5 | WL-1-ALT-GB1 | 0

## Brakes & Jacks
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Brakes & Jacks | Component | O-27611-002 | 1 | Brake |  | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 2 | Cylinder |  | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 3 | Base Plate |  | 2 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 4 | Plate |  | 2 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 5 | Plate |  | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 6 | Piston |  | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 7 | Guide ring |  | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 8 | Grooved ring collar |  | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 9 | Nut |  | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 10 | Disc spring |  | 3 |  | Need details when in workshop? | [5 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 11 | Piston |  | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-002 | 12 | Guide part |  | 2 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Fastener | O-27611-002 | 13 | Cap head screw | M8 x 15mm, plain steel, grade? | 2 | For item 12 | [6 empty] | n/a | WL-1-ALT-BJA | 0
Brakes & Jacks | Fastener | O-27611-002 | 14 | Lock washer | ? | 2 | For item 12 | [6 empty] | n/a | WL-1-ALT-BJA | 0
Brakes & Jacks | Dowel | O-27611-002 | 15 | Nut |  | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Dowel | O-27611-002 | 16 | Dowel pin |  | 4 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks |  | O-27611-002 | 17 | ? |  | 3 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-003 | 18 | Spring for Brake Shoe |  | 2 |  | Need details when in workshop? | [5 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-003 | 19 | Eye bolt for Spring | M10 x 70mm | 2 | For item 18 | [6 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-003 | 20 | Nut | M10, plain steel | 2 | For item 19 | [6 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-003 | 21 | Washer | M10 | 2 | For item 20 | [6 empty] | N/A | WL-1-ALT-BJA | 0
Brakes & Jacks | Fastener | O-27611-003 | 22 | Hex Screw for Fixing Brake | M24 X 55mm, Z/P, class 5.6 | 16 |  |  | Y | Site | Josh | Y |  | Tub 1 | WL-1-ALT-BJA | 0
Brakes & Jacks | Nordlock | O-27611-003 | 23 | Flat Washer | 24mm Nordlock Washer, Z/P | 16 | For item 22 |  | Y | Site | Josh | Y |  | Tub 1 | WL-1-ALT-BJA | 0
Brakes & Jacks | Component | O-27611-003 | 25 | Molycote for Piston Lubrication | Molycote GN Paste | 1 | [7 empty] | N/A | WL-1-ALT-BJA | 0
Jacking Pump | Fastener | O-27917 | N/A | Hex Bolt for Jacking Pump Foot | 3/8" BSW, 1" Long, Plain Steel (ZP) | 4 | For item 13 on drawing O-27917 |  | Y | Site | Josh | Y |  | Tub 1 | WL-1-ALT-BJA | 0
Jacking Pump | Fastener | O-27917 | N/A | Hex bolt for Jacking Pump Motor | M12 x 30mm, Z/P, class 5.6 | 4 | For item 13 on drawing O-27917 |  | Y | Site | Josh | Y |  | Tub 1 | WL-1-ALT-BJA | 0

## Lower Bracket
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Lower Bracket | Component | O-27314-002 | 1 | Lower bracket |  | 1 | Makers Drawing |  | Y | Cambridge | Matt |  |  | N/A | WL-1-ALT-GB1 | 0
Lower Bracket | Component | O-27314-003 | 21 | Oil sight glass |  | 1 |  | Need info? | Y | Cambridge | Matt/Tom | N/A |  | Installed | WL-1-ALT-GB1 | 0
Lower Bracket | Component | O-27609-002 | 1 | Lower bracket |  | 1 | Assembly Drawing |  | Y | Cambridge | Matt/Tom | N/A |  | Loading Bay | WL-1-ALT-GB1 | 0
Lower Bracket | Component | O-27609-002 | 2 | Lower Bracket Shim - 1mm | 1mm Shim plate, plain steel | 8 | For setting of Lower Bracket RL and Level |  | Y | Site | Tom | Y |  | Inward Goods Store | WL-1-ALT-GB1 | TBC
Lower Bracket | Component | O-27609-002 | 3 | Lower Bracket Shim - 1mm | 2mm Shim plate, plain steel | 8 | For setting of Lower Bracket RL and Level |  | Y | Site | Tom | Y |  | Inward Goods Store | WL-1-ALT-GB1 | TBC
Lower Bracket | Component | O-27609-002 | 4 | Lower Bracket Shim - 1mm | 3mm Shim plate, plain steel | 4 | For setting of Lower Bracket RL and Level |  | Y | Site | Tom | Y |  | Inward Goods Store | WL-1-ALT-GB1 | TBC
Lower Bracket | Component | O-27609-002 | 5 | Nipple for Air Sampling |  | 1 |  | Check if still needed? | N | Site | Tom | N |  | ? | WL-1-ALT-GB1 | 0
Lower Bracket | Seal | O-27609-002 | 6 | Lower Bracket Top Cover Oring | 8mm Oring, 70 Shore | 1 |  | Need to confirm shore hardness? | Y | Site | Tom | Y ? |  | Tub 1 | WL-1-ALT-GB1 | 0
Lower Bracket | Fastener | O-27609-002 | 7 | Hex Screw for Lower Bracket | M42 x 70mm, Z/P, class 5.6 | 8 |  |  | Y | Site | Tom | Y |  | Tub 2 | WL-1-ALT-GB1 | 0
Lower Bracket | Nordlock | O-27609-002 | 8 | Lower Bracket hold down bolt Locking Plate | 42mm Nordlock Washer, Z/P | 8 |  | Confirm is Nordlocks will be used? | N | Site | Tom | Y |  | Tub 2 | WL-1-ALT-GB1 | 0
Lower Bracket | Component | O-27609-002 | 9 | Screw plug |  | 1 |  | Need to confirm what this is for? | N | Cambridge | Matt/Tom | N |  | ? | WL-1-ALT-GB1 | 0
Lower Bracket | Dowel | O-27609-002 | 10 | Lower Bracket Taper Pin | 30mm x 120mm, 4140 | 8 |  |  | N | Site | Tom | Y ? |  | Tub 2 | WL-1-ALT-GB1 | 0
Lower Bracket | Dowel | O-27609-002 | 11 | Washer for Taper Pin | 24mm Washer, plain steel | 8 |  |  | N | Site | Tom |  |  | N/A | WL-1-ALT-GB1 | 0
Lower Bracket | Dowel | O-27609-002 | 12 | Hexagon nut for Taper Pin | M24 Nut, plain steel, class 5.6 | 8 |  |  | N | Site | Tom |  |  | N/A | WL-1-ALT-GB1 | 0
Lower Bracket | Component | O-27609-002 | 13 | Disk |  | 1 |  | Need to confirm what this is for? | N | Cambridge | Matt/Tom |  |  | N/A | WL-1-ALT-GB1 | 0
Covering | Component | O-27316-002 | 1 | Lower Guide Bearing Bracket Bottom Cover | Segment type 1 (sections 3 and 6) | 2 |  | Confirm if part of workshop scope? | N | Cambridge | Matt | N/A |  | Installed | WL-1-ALT-GB1 | 0
Covering | Component | O-27316-002 | 2 | Lower Guide Bearing Bracket Bottom Cover | Segment type 2 (section 2 and 3) |  |  | Confirm if part of workshop scope? | N | Cambridge | Matt | N/A |  | Installed | WL-1-ALT-GB1 | 0
Covering | Component | O-27316-002 | 3 | Lower Guide Bearing Bracket Bottom Cover | Segment type 3 (section 4 and 5) |  |  | Confirm if part of workshop scope? | N | Cambridge | Matt | N/A |  | Installed | WL-1-ALT-GB1 | 0
Covering | Component | O-27316-002 | 4 | Lower Guide Bearing Bracket Vertical Cover |  | 4 |  | Confirm if part of workshop scope? | N | Cambridge | Matt | N/A |  | Forecourt Racking | WL-1-ALT-GB1 | 0
Covering | Component | O-27316-002 | 5 | Lower Guide Bearing Bracket Vertical Cover Angle Support |  | 4 |  | Confirm if part of workshop scope? | N | Site | Jeremy | N/A |  | Installed | WL-1-ALT-GB1 | 0
Covering | Fastener | O-27316-002 | 11 | Lower Guide Bearing Bracket Cover Screw | M10 X 18mm, Z/P, class 5.6 | 92 |  | Confirm grade? | Y | Site | Josh | Y |  | Tub 3 | WL-1-ALT-GB1 | 0
Covering | Nordlock | O-27316-002 | 12 | Lower Guide Bearing Bracket Cover screw lock washer | 10mm Nordlock Washer, Z/P | 92 | For item 11 | Replace with Nordlock? | Y | Site | Josh | Y |  | Tub 3 | WL-1-ALT-GB1 | 0
Covering | Component | O-27316-002 | 13 | Lower Guide Bearing Bracket Vertical Cover Handle |  | 8 | For item 4 |  | Y | Cambridge | Matt/Tom |  |  | N/A | WL-1-ALT-GB1 | 0

## Runner and Turbine Shaft
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Runner | Component | O-27256 | 1 | Runner | Runner | 1 |  |  | Y | Cambridge | Matt | N/A | Y | Installed | WL-1-TUR-RUN | 0
Runner | Component | O-27256 | 2 | Wearing ring | Wearing ring O-60616 | 1 | The runner wearing ring wasn’t replaced so should be a spare?? |  | Y |  |  |  |  | N/A | WL-1-TUR-RUN | 1
Runner | Component | O-27256 | 3 | Runner Drive Pin | Drive Pin For Runner to Thurbine Shaft | 6 |  | Confirm Location? | Y | Cambridge | Matt | Y | Y | Installed | WL-1-TUR-RUN | 0
Runner | Fastener | O-27256 | 7 | Hex Screw for Runner Drive Pin Keeper | M12 X 20mm Hex Head Screw, Class C1-50 | 12 |  | Change to Stainless | N | Site | Josh | N | N | Tub 1 | WL-1-TUR-RUN | 0
Runner | Tab Washer | O-27256 | 8 | Tab Washer for Runner Drive Pin Keeper Screws | 12mm Din? | 6 | For item 7 | Confirm Din? | N | Site | Josh | Y | N | Tub 1 | WL-1-TUR-RUN | 0
Turbine shaft | Component | O-27718 | 1 | Turbine shaft | Turbine shaft | 1 |  |  | Y | Hoffmans | Matt | N/A | Y | Loading Bay | WL-1-TUR-SHT | 0
Turbine shaft | Component | O-27718 | 2 | Coupling bolt | Turbine Shaft to Generator Shaft Bolts | 12 | Re-use | Confirm Details? | Y | Site | Tom | N/A | N/A | Mezzanine | WL-1-TUR-SHT | 0
Turbine shaft | Component | O-27718 | 3 | Nut | Nuts for Turbine Shaft to Generator Shaft Bolts | 12 | For item 2 | Confirm Details? | N | Site | Tom | N/A | N/A | Mezzanine | WL-1-TUR-SHT | 0
Turbine shaft | Component | O-27718 | 4 | Blind cover | Cover for Bottom of Turbine Shaft | 1 | For item 1 |  | Y | Site | Jeremy | N/A | N/A | Parts Container | WL-1-TUR-SHT | 0
Turbine shaft | Fastener | O-27718 | N/A | Hex Bolts for Blind Cover | M16 X 45mm Hex Head Bolt, Class C1-50 | 6 | For item 4 | Change to Stainless | Y | Site | Josh | Y | N | Tub 1 | WL-1-TUR-SHT | 0
Turbine shaft | Tab Washer | O-27718 | N/A | Locking Tabs for Hex Bolts | 17mm Din 432 | 6 | For item 4 |  | Y | Site | Josh | Y | N | Tub 1 | WL-1-TUR-SHT | 0
Turbine shaft | Fastener | O-27718 | N/A | Hex Bolt for Plugging Lifting Point in Blind Cover | M36 X 50mm Hex Head Bolt, Class C1-50 | 1 | For item 4 |  | Y | Site | Josh | Y | N | Tub 1 | WL-1-TUR-SHT | 0
Turbine shaft | Seal | O-25849 | N/A | O-ring for Blind Cover | 6mm, 70 Shore | 1 | For item 4 | Confirm? | N | Site | Tom | N | N | Tub 1 | WL-1-TUR-SHT | 0
Turbine shaft | Tab Washer | O-27718 | 5 | Pawl washer | 68mm Din? | 12 | For item 2 | Confirm New Requirements? | N | Site | Jeremy | N | N | ? | WL-1-TUR-SHT | 0
Turbine shaft | Component | O-27718 | 6 | Locking pin | ? | 12 |  | Confirm Why this is there? | N | Site | Tom | N | N | ? | WL-1-TUR-SHT | 0
Turbine shaft | Component | O-27718 | 7 | Stud for Runner Coupling | M58 x 2mm Pitch, Stainless Steel | 6 |  | Confirm Details? | Y | Voith | Tom | N/A | Y | Installed | WL-1-TUR-SHT | 0
Turbine shaft | Component | O-27718 | 8 | Nut for Runner Coupling Stud | M58 x 2mm Pitch, Stainless Steel | 6 |  | Confirm Details? | Y | Voith | Tom | N/A | Y | Installed | WL-1-TUR-SHT | 0
Nose Cone | Component | O-25849 | 25 | Runner Nose Cone | Runner Nose Cone |  | See Drawing O-27684 for details |  | Y | Firmins | Matt | N/A | N | Firmans | WL-1-TUR-RUN | 0
Nose Cone | Fastener | O-27256 | 4 | Hex Bolt for Runner Nose Cone | M20 X 55mm Hex Bolt, Class C1-50 | 8 | For item 25 on drawing O-25849 | Change to Stainless and Bolt | Y | Site | Josh | Y | N | Tub 2 | WL-1-TUR-RUN | 0
Nose Cone | Fastener | O-27256 | 5 | Nuts for Runner Nose Cone Studs | M20, Z/P, Class A4-80 | 8 | For item 4 | Change to Stainless. | Y |  |  |  |  | N/A | WL-1-TUR-RUN | 0
Nose Cone | Tab Washer | O-27256 | 6 | Tab Washer for Runner Nose Cone Studs | 20mm Din 432, Stainless Steel | 8 | For item 4 |  | Y | Site | Josh | Y | N | Tub 2 | WL-1-TUR-RUN | 0
Turbine Shaft Coupling | Component | O-25849 | 36 | Coupling Cover - Generator Side | Coupling Cover for Turbine Shaft and Generator Coupling Bolts | 1 |  |  | Y | Site | Jeremy | N/A | N/A | Mezzanine | WL-1-TUR-SHT | 0
Turbine Shaft Coupling | Component | O-25849 | 37 | Coupling Cover - Turbine Side | Coupling Cover for Turbine Shaft and Generator Coupling Bolts | 1 | For items 36 and 37 |  | Y | Site | Jeremy | N/A | N/A | Mezzanine | WL-1-TUR-SHT | 0
Turbine Shaft Coupling | Fastener | N/A | N/A | Capscrew for Coupling Cover | M16 X 30mm Lowhead SH Capscrew, Z/P, class 8.8 | 24 | Option 1 |  | Y | Site | Josh | N | N | N/A | WL-1-TUR-SHT | 0
Turbine Shaft Coupling | Fastener | N/A | N/A | Capscrew for Coupling Cover | M16 X 30mm SH Capscrew, Z/P, class 12.9 | 24 | Option 2 |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-TUR-SHT | 0
Turbine Shaft Coupling | Nordlock | N/A | N/A | Nordlock for Coupling Cover Capscrew | 16mm Nordlock Washer, Z/P | 24 | For Option 2 | Confirm if required? | Y | Site | Josh | Y | Y | Tub 3 | WL-1-TUR-SHT | 0
Turbine Shaft Coupling | Fastener | N/A | N/A | Bolt for Coupling Cover Joints | M16 X 60mm Stud Z/P, class 8.8 | 4 | For items 36 and 37 |  | Y | Site | Josh | Y | N | Tub 3 | WL-1-TUR-SHT | 0
Turbine Shaft Coupling | Fastener | N/A | N/A | Nut for Coupling Cover Joints Bolts | M16, Z/P, Class 8 | 4 |  |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-TUR-SHT | 0
Turbine Shaft Coupling | Tab Washer | N/A | N/A | Tab Washer for Coupling Cover Joints Bolts and Nuts | 16mm Din 93 | 8 |  |  | Y | Site | Josh | Y | N | Tub 3 | WL-1-TUR-SHT | 0

## Spiral Casing
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Spiral Casing Cover | Component | O-27929 | 1 | Man hole cover |  | 1 | Weight = 160Kg |  | Y |  |  | N/A | Y | Mezzanine | WL-1-TUR-SPR | 0
Spiral Casing Cover | Seal | O-27929 | 6 | Round rubber packing | 7mm, 70 Shore | 1 |  | Confirm size and Shore? | N | Site | Tom | Y | Y | Tub 1 | WL-1-TUR-SPR | 0
Spiral Casing Cover | Fastener | O-27929 | 7 | Bolts for Spiral Casing Cover | M30 x 80mm, Z/P, Class 8.8 | 16 |  | changed to 8.8 Z/P | Y |  | Tom | Y | Y | Tub 1 | WL-1-TUR-SPR | 0
Spiral Casing Cover | Nordlock | O-27929 | N/A | Nordlock Washers for Spiral Casing CoverBolts | 30mm Nordlock Washer, Z/P | 16 | For item 7 | Add Nordlock | Y |  | Tom | Y | Y | Tub 1 | WL-1-TUR-SPR | 0
Turbine Walkway | Fastener | N/A | N/A | Turbine Walkway Screws | M10 x 25 Counter Sunk Screw, Z/P | 180 |  | Confirm details? | Y |  | Josh | Y | Y | Tub 2 | WL-1-TUR-SPR | 0
Turbine Walkway | Fastener | N/A | N/A | Turbine Walkway Handrail | M12 x 25, Hex Head Bolts, Z/P, Class 4.6 | 12 |  | Confirm details? | Y |  | Josh | N | N | Tub 2 | WL-1-TUR-SPR | 0

## Upper & Lower Fan Rings
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Fan Blade | Component | O-27006-002 | 1 | Non Drive Side Fan Ring | Top Fan Blade | 10 |  | Y | Site | Josh | N/A | Y | Mezzanine | WL-1-ALT-ROT | 0
Fan Blade | Component | O-27006-002 | 2 | Drive Side Fan Ring | Bottom Fan Blade | 10 |  | Y | Site | Josh | N/A | Y | Mezzanine | WL-1-ALT-ROT | 0
Fan Blade | Component | O-27006-002 | 3 | Washer | Special Washer for Fan Blade Screws | 40 |  | Y | Site | Josh | N/A | Y | Tub 1 | WL-1-ALT-ROT | 0
Fan Blade | Tab Washer | O-27006-002 | 4 | Tab Washer for Fan Blade Screws | 16mm Din 93 Z/P | 40 |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-ROT | 0
Fan Blade | Fastener | O-27006-002 | 5 | Hex screw for Fan Blades | M16 X 40mm Hex Head Screw, Z/P, Class 8.8 | 40 |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-ROT | 0
Fan drive side | Component | O-27133-002 | 3 | Brake ring |  | 1 | [6 empty] | N/A | WL-1-ALT-ROT | 0
Fan drive side | Component | O-27133-002 | 7 | Pin For Brake Track | Dowel for Brake Track to Fan Ring | 5 | [6 empty] | N/A | WL-1-ALT-ROT | 0
Fan drive side | Fastener | O-27133-002 | 9 | Cheese head screw | M10 X 25? | 5 | For Securing Brake Track Dowel item 7 | [5 empty] | N/A | WL-1-ALT-ROT | 0
Fan drive side | Fastener | O-27133-002 | 10 | Hex bolt for Brake Track | M24 x 65mm Hex Head Bolt, Z/P, Class 5.6 | 10 | For securing Brake Track to Fan Ring | Y |  |  |  |  | N/A | WL-1-ALT-ROT | 0
Fan drive side | Tab Washer | O-27133-002 | 11 | Locking plate | 25mm Din 432 | 10 | For item 10 | [5 empty] | N/A | WL-1-ALT-ROT | 0
Fan drive side | Component | O-27133-002 | 12 | Bushing for Lower Fan Ring Bolts | 25 x 48 | 10 |  | Y | Site | Josh | N/A | Y | Tub 1 | WL-1-ALT-ROT | 0
Fan drive side | Fastener | O-27636 | 55 | Bolt for Lower Fan Ring | M24 x 90mm Hex Head Bolt, Plain Steel, Class 5.6 | 10 | For Securing Lower Fan Ring to Rotor | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-ROT | 0
Fan drive side | Tab Washer | O-27636 | 64 | Tab Washer for Lower Fan Ring Bolts | 25mm Din 432 | 10 | For item 55 | Y | Site | Josh | Y | Y | Tub 1 | WL-1-ALT-ROT | 0
Fan nondrive side | Fastener | O-27198-002 | N/A | Nut for Top Fan Ring | M36 Castle Nut, Plain Steel, Class 5.6 | 10 | For Secuing Fan Ring to Rotor | Y | Site | Josh | N/A | Y | Tub 1 | WL-1-ALT-ROT | 0
Fan nondrive side | Fastener | O-27198-002 | N/A | Split Pin for Top Fan Ring Nut | 4.5mm x 80mm long, plain steel Split Pin | 10 | For securing Castle Nut | Y | Site | Josh | Y | N | Tub 1 | WL-1-ALT-ROT | 0

## Draft Tube
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Draft Tube Liner | Fastener | O-27715 | N/A | Hex Bolt for Draft Tube Liner to Bottom Cover | M24 x 60mm Hex Bolt, Z/P, Class 4.6 | 24 |  | Changed length due to Nordlock Confirm if nuts are needed? | N | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Nordlock | O-27715 | N/A | Nordlock for Draft Tube Liner to Bottom Cover Bolts | 24mm Nordlock Washer, Z/P | 24 |  | Added Nordlock | N | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Seal | O-25574 | N/A | Oring for Draft Tube Liner to Bottom Cover | 9mm, 70 Shore | 1 |  |  | N | Site | Tom | N |  | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Seal | O-25574 | N/A | Oring for Draft Tube Sliding Ring to Draft Tube | 9mm, 70 Shore | 1 |  |  | N | Site | Tom | N |  | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Seal | O-25574 | N/A | Oring for Draft Tube Liner to Sliding Ring | 9mm, 70 Shore | 1 |  |  | N | Site | Tom | N |  | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Fastener | O-33541 | N/A | Hex Bolt for Draft Tube Liner to Draft Tube | M24 x 100mm Hex Bolt, Z/P, Class 4.6 | 24 |  | Changed length due to Nordlock | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Fastener | O-33541 | N/A | Hex Nut for Draft Tube Liner to Draft Tube Bolt | M24 Hex Nut Z/P, Class 5 | 24 |  |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Nordlock | O-33541 | N/A | Nordlock for Draft Tube Liner to Draft Tube Bolt | 24mm Nordlock Washer, Z/P | 48 |  | Added Nordlock | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Fastener | O-33542 | 3 | Hex Bolt for Draft Tube Liner Slip Flange | M24 x 130mm Hex Bolt, Z/P, Class 4.6 | 8 |  |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Fastener | O-33542 | 4 | Hex Nut for Draft Tube Liner Slip Flange Bolt | M24 Hex Nut Z/P, Class 5 | 8 |  |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-DTU | 0
Draft Tube Liner | Nordlock | O-33542 | N/A | Nordlock for Draft Tube Liner Slip Flange Bolt | 24mm Nordlock Washer, Z/P | 16 |  |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-DTU | 0
Man Hole | Fastener | O-60248 | N/A | Hex Bolt for Draft Tube Man Hole | M24 x 45mm Hex Bolt, Z/P, Class 4.6 | 8 |  |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-DTU | 0
Man Hole | Nordlock | O-60248 | N/A | Nordlock for Draft Tube Man Hole Bolt | M24 Hex Nut Z/P, Class 5 | 8 |  |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-DTU | 0
Platform Covers | Fastener | O-60248 | N/A | Hex Bolt for Draft tube Platform mounts | M12 x 30mm Hex Bolt, Z/P, Class 4.6 | 16 |  |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-DTU | 0
Platform Covers | Nordlock | O-60248 | N/A | Nordlock for Draft tube Platform mounts Bolt | 12mm Nordlock Washer, Z/P | 16 |  |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-DTU | 0
Blanking Flange | Fastener | O-60248 | N/A | Bolt for Blanking Flanges | M16 x 40mm Hex Bolt, Z/P, Class 4.6 | 16 |  |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-DTU | 0
Blanking Flange | Nordlock | O-60248 | N/A | Nordlock for Blanking Flange Bolts | 16mm Nordlock Washer, Z/P | 16 |  |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-DTU | 0

## Turbine Guide Bearing
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Inner Oil Reservoir | Component | O-25849 | 40 | Inner Oil Reservoir | Inner Oil Reservoir for TGB | 1 |  |  | Y | Cambridge | Matt | N/A | Y | On Turbine Shaft | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Component | O-25849 | 41 | Inner Oil Reservoir Connecting Plate | Connecting Plate between Oil Reservoir and TGB Support | 1 |  |  | Y | Cambridge | Matt | N/A | Y | Gowrie Park | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Fastener | O-27719 | N/A | Inner Screw for Connecting Plate | M12 X 30mm Hex Screw,plain steel, grade 4.6 | 20 | For Inner Oil Reservoir to Connecting Plate | For item 40 on drawing O-25849 | Y | Site | Josh | Y |  | Tub 1 | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Nordlock | O-27719 | N/A | Nordlock for Connecting Plate Inner Screw | 12mm Nordlock Washer, S/S | 20 |  | For item 40 on drawing O-25849 | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Fastener | O-27719 | N/A | Outer Screw for Connecting Plate | M12 X 30mm Hex Screw, plain steel, grade 4.6 | 24 | For Connecting Plate to TGB Support | For item 41 on drawing O-25849 | Y | Site | Josh | Y |  | Tub 1 | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Nordlock | O-27719 | N/A | Nordlock for Connecting Plate Outer Screw | 12mm Nordlock Washer, S/S | 24 |  | For item 41 on drawing O-25849 | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Fastener | O-25849 | N/A | Bolts for Connecting Plate Joint | M16 x 55mm Hex Bolt, Plain Steel, Class 4.6 | 4 |  | Longer bolt due to Nordlock | Y | Site | Josh | Y |  | Tub 1 | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Fastener | O-25849 | N/A | Nuts for Connecting Plate Joint Bolts | M16 Nut, Plain Steel, Class 5 | 4 |  |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Fastener | O-25849 | N/A | Nordlocks for Connecting Plate Joint Bolts | 16mm Nordlock Washer, S/S | 8 |  |  | Y | Site | Josh | Y | Y | Tub 1 | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Seal | O-25849 | N/A | Inner Oring for Connecting Plate | 5mm, 70 Shore | 1 | For Inner Oil Reservoir to Connecting Plate | Confirm Shore? | N | Site | Tom | Y |  | Tub 1 | WL-1-TUR-GB1 | 0
Inner Oil Reservoir | Seal | O-27713 Rev:B | 14 | Outer Oring for Connecting Plate | 5mm, 70 Shore | 1 | For Connecting Plate to TGB Support | Confirm Shore? | N | Site | Tom | Y |  | Tub 1 | WL-1-TUR-GB1 | 0
TGB Cover | Component | O-25849 | 43 | Turbine Bearing Top Cover | Turbine Bearing Top Cover | 1 |  |  | Y | Cambridge | Matt | N/A |  | Cethana | WL-1-TUR-GB1 | 0
TGB Cover | Fastener | O-27716 Rev:B | 9 | Bolt for Turbine Bearing Cover Joint | M16 X 55mm Hex Head Bolt, grade 4.6 | 8 |  | Changed to 4.6, Longer bolt due to Nordlock | Y | Site | Josh | Y |  | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Fastener | O-27716 Rev:B | 10 | Nut for Turbine Bearing Cover Joint Bolt | M16, Z/P, Class 5 | 8 | For item 9 |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Nordlock | O-27716 Rev:B | N/A | Nordlock for Turbine Bearing Cover Joint Bolt | 16mm Nordlock Washer, Z/P | 16 |  |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Dowel | O-27716 Rev:B | 11 | Turbine Bearing Cover Joint Taper Pin | 10mm x xxmm ? | 4 |  |  | N | Cambridge | Matt | N/A |  | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Fastener | O-27716 Rev:B | 12 | Bolt for Turbine Bearing Cover | M16 X 35mm Hex Head Bolt, plain steel, grade 4.6 | 16 |  | Changed to 4.6, Longer bolt due to Nordlock | Y | Site | Josh | Y |  | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Nordlock | O-27716 Rev:B | N/A | Nordlock for Turbine Bearing Cover Bolt | 16mm Nordlock Washer, Z/P | 16 |  |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Component | O-27716 Rev:B | 13 | Blind cover? |  | 2 |  | Looks like inspection Cover | N | Cambridge | Matt | N/A |  | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Component | O-27716 Rev:B | 14 | Liner for Labyrinth Ring | Liner for TGB Labyrinth Ring | 2 | For item 15 Also item 44 on O-25849 |  | Y | Cambridge | Matt | N/A | Y | Gowrie Park | WL-1-TUR-GB1 | 0
TGB Cover | Component | O-27716 Rev:B | 15 | Turbine Bearing Cover Labyrinth ring | Turbine Bearing Cover Labyrinth ring | 2 |  |  | Y | Cambridge | Matt | N/A | Y | Gowrie Park | WL-1-TUR-GB1 | 0
TGB Cover | Fastener | O-27716 Rev:B | 17 | Bolt for Blind Cover | M12 x 25 Hex Head Bolt, Z/P, Class 4.6 | 8 | For item 13 | Changed to 4.6, Longer bolt due to Nordlock | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Nordlock | O-27716 Rev:B | 17 | Nordlock for Blind Cover Bolt | 12mm Nordlock Washer, Z/P | 8 | For item 17 |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Fastener | O-27716 Rev:B | N/A | Bolt Turbine Bearing Cover Labyrinth Ring | M12 x 65 Hex Head Bolt, Z/P, Class 4.6 | 12 | For item 14 and 15 | Changed to 4.6, Longer bolt due to Nordlock | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-GB1 | 0
TGB Cover | Fastener | O-27716 Rev:B | N/A | Nordlock for Turbine Bearing Cover Labyrinth Ring Bolt | 12mm Nordlock Washer, Z/P | 12 | For item 14 and 15 |  | Y | Site | Josh | Y | Y | Tub 2 | WL-1-TUR-GB1 | 0
TGB Support | Component | O-25849 | 42 | Turbine Bearing Support | Turbine Bearing Support | 1 |  |  | Y | Cambridge | Matt | N/A |  | Cethana | WL-1-TUR-GB1 | 0
TGB Support | Seal | O-27713 Rev:B | 14 | Turbine Guide Bearing Oil Pot Sleeve Connection Piece Oring | xxmm, xx shore Oring ? | 1 |  | Need to check size, drawing looks like 5mm | N | Site | Tom | N | N | Tub 1 | WL-1-TUR-GB1 | 0
TGB Support | Dowel | O-27713 Rev:B | 18 | Turbine Bearing Support, Taper Pin | 20 x 120 | 4 |  | Make New Parralel 24mm? | N | Site | Josh | N | N | Tub 3 | WL-1-TUR-GB1 | 0
TGB Support | Dowel | O-27713 Rev:B | 19 | Nut for Taper Pin | M16 | 4 | For item 18 |  | N | Site |  |  |  | N/A | WL-1-TUR-GB1 | 0
TGB Support | Dowel | O-27713 Rev:B | 20 | Washer for Taper Pin | M16 | 4 | For item 18 |  | N |  |  |  |  | N/A | WL-1-TUR-GB1 | 0
TGB Support | Fastener | O-27712 | 27 | Hex Bolt for Turbine Bearing Support | M36 X 70mm Hex Bolt, Z/P, Class 5.8 | 24 | May be used instead of Studs, depending on availability | Changed to Bolt and 8.8 | Y | Site | Josh | Y | N | Tub 3 | WL-1-TUR-GB1 | 0
TGB Support | Fastener | O-27712 | 27 | Stud for Turbine Bearing Support | M36 X 115mm Stud Bolt, Z/P, Class 5.8 | 24 | For item 42 on drawing O-25849 | Change to Bolt? 70mm Long? | Y | Site | Josh | Y | N | Tub 3 | WL-1-TUR-GB1 | 0
TGB Support | Fastener | O-27712 | 28 | Nut for Turbine Bearing Support Stud | M36, Z/P | 24 | For item 27 |  | Y | Site | Josh | Y | N | Tub 3 | WL-1-TUR-GB1 | 0
TGB Support | Nordlock | O-27712 | N/A | Nordlock for Turbine Bearing Support Stud | 36mm Nordlock Washer, Z/P | 24 | For item 27 |  | Y | Site | Josh | Y | Y | Tub 3 | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Fastener | O-27713 Rev:B | 15 | Stud for Turbine Bearing | M30 X 65mm Stud Bolt, plain steel, Class 4.6 | 20 |  | Changed to 4.6 | N | Cambridge | Matt | N | N | Tub 4 | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Fastener | O-27713 Rev:B | 16 | Nut for Turbine Bearing Stud | M30 Plain Steel, Class 4.6 | 20 |  | Changed to 4.6 | N | Cambridge | Matt | N | N | Tub 4 | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Nordlock | O-27713 Rev:B | 17 | Nordlock for Turbine Bearing Stud | 30mm Nordlock Washer, S/S | 20 |  | Changed to 4.6 | N | Cambridge | Matt | N | N | Tub 4 | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 1 | ? |  | 2 |  | Need to get Mandy to lighten draing so we can see it better | [5 empty] | N/A | WL-1-TUR-GB1 | 2?
Turbine Guide Bearing | Component | O-27717 Rev:B | 2 | ? |  | 2 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 3 | ? |  | 1 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 4 | ? |  | 1 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 5 | ? |  | 2 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 6 | ? |  | 6 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 7 | ? |  | 10 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 8 | ? |  | 4 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 9 | ? |  | 2 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 10 | ? |  | 2 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 11 | ? |  | 3 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Fastener | O-27717 Rev:B | 12 | Fitted bolts for Turbine Bearing Joint | M24 X 105mm hex fitted bolt , plain steel, Class 4.6 | 4 |  |  | N | Cambridge | Matt | N | N | Tub 4 | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 13 | Hex for Turbine Bearing Joint Bolts | M24 Plain Steel, Class 4.6 | 16 | For item 14 and 12 |  | N | Cambridge | Matt | N | N | Tub 4 | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 14 | Hex Bolt for Turbine Bearing Joint | M24 X 105mm hex bolt, plain steel, Class 4.6 | 4 |  |  | N | Cambridge | Matt | N | N | Tub 4 | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | N/A | Nordlock for Turbine Bearing Joint Bolts | 24mm Nordlock Washer, S/S |  |  |  | N | Cambridge | Matt | N | N | Tub 4 | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 15 | ? |  | 1 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 16 | Plug? |  | 1 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 17 | Bind? |  | 12 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 18 | Blind? |  | 12 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 19 | Plug? |  | 2 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 20 | ? |  | 2 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Dowel | O-27717 Rev:B | 21 | Dowel Pin for Turbine Bearing | 20mm x 80mm | 2 |  |  | N | Cambridge | Matt | N | N | Tub 4 | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 22 | Pipe? |  | 6 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Component | O-27717 Rev:B | 23 | Suction pipe? |  | 6 | [7 empty] | N/A | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Pickup Pipe | O-25849 | N/A | TGB Oil Pickup Pipes | TGB Oil Pickup Pipes | 6 | [8 empty] | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Oil Screen | O-25849 | 39 | Oil Screen for TGB | Oil Screen for TGB | 1 | in halves | [7 empty] | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Dowel | O-25849 | N/A | Dowel for oil screen | Dowel for oil screen | 2 | [8 empty] | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Caphead | O-25849 | N/A | Oil Screen Split join caphead | M10 x 35 Gr12.9 | 4 | [8 empty] | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Nordlock | O-25849 | N/A | Nordlock for split join capheads | NL10 S.S | 4 | [8 empty] | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Fastener | O-25849 | N/A | Hex Bolt for Oil screen | M10 x 35 Gr 8.8 | 16 | Oil Screen to bearing fastener | [7 empty] | WL-1-TUR-GB1 | 0
Turbine Guide Bearing | Nordlock | O-25849 | N/A | Nordlock for Oil Screen to TGB Fasteners | NL10 S.S | 16 | [8 empty] | WL-1-TUR-GB1 | 0
Oil Level Device | Component | A2-07831-020 | 59 | Oil Level Sight Glass | Oil Level Sight Glass - Alemlube FGB2200 | 1 | Spare is for glass tube only | [7 empty] | WL-1-TUR-GB1 | 1
TGB Cooler | Component | O-26404 | 1 | Cooler Calibration Tube | Cooler Calibration Tube 11ODx1Thk 90/10 CuNi | 1 | [8 empty] | WL-1-TUR-GB1-HTX | 1

## Brushgear
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Slip rings | Component | O-26343-002 |  | Slipring |  | 1 |  | No Part Number on Drawing | [5 empty] | Cambridge | WL-1-EXS-BGR | 0
Slip rings | Component | O-26343-002 | 5 | Speical Bolt for Clapming Slip Rings | A=303, B=197 | 8 | [7 empty] | Cambridge | WL-1-EXS-BGR | 0
Slip rings | Component | O-26343-002 | 6 | Connecting bolt |  | 1 | [7 empty] | Cambridge | WL-1-EXS-BGR | 0
Slip rings | Component | O-26343-002 | 7 | Connecting bolt |  | 1 | [7 empty] | Cambridge | WL-1-EXS-BGR | 0
Slip rings | Component | O-26343-002 | 8 | Insulating tube |  | 1 | [7 empty] | Cambridge | WL-1-EXS-BGR | 0
Slip rings | Component | O-26343-002 | 9 | Spacer |  | 16 | [7 empty] | Cambridge | WL-1-EXS-BGR | 0
Slip rings |  | O-26343-002 | 10 | ? |  | 8 | [8 empty] | WL-1-EXS-BGR | 0
Slip rings | Component | O-26343-002 | 11 | Pressboard sheet | [9 empty] | N/A | WL-1-EXS-BGR | 0
Slip rings | Fastener | O-26343-002 | 12 | Castle nut for Clamping of Slip Rings | M30 Castle Nut, Plain Steel, Class 5 | 8 | For item 5 | [6 empty] | N/A | WL-1-EXS-BGR | 0
Slip rings | Fastener | O-26343-002 | 13 | Hex Nut for Clamping of Slip Rings | M24 | 8 | For item 5 | [6 empty] | N/A | WL-1-EXS-BGR | 0
Slip rings | Fastener | O-26343-002 | 14 | Washer For Castle nut | 30mm Washer Extra Thick, Plain Steel | 8 | For item 12 | [6 empty] | N/A | WL-1-EXS-BGR | 0
Slip rings | Fastener | O-26343-002 | 15 | Split Pin for Castle Nut | 6x55 Split Pin, Plain Steel | 8 | For item 12 | [6 empty] | N/A | WL-1-EXS-BGR | 0
Slip rings | Fastener | O-26343-002 | 16 | Hex screw for Slingrings | M20 x 55mm Hex Screw, Plain Steel, Class 5.6 | 8 |  | Changed length due to Nordlock | Y |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Slip rings | Fastener | O-26343-002 | 17 | Nordlock for Slingrings Screws | 20mm Nordlock Washer, Z/P | 8 |  | Change from Din 93 to Nordlock | Y |  |  | Y | Y | Tub 1 | WL-1-EXS-BGR | 0
Brush carrier | Component | O-26763-002 | 4 | Special Bolt For Brushgear | Special Bolt For Brushgear | 5 | [7 empty] | Cambridge | WL-1-EXS-BGR | 0
Brush carrier | Component | O-26763-002 | 5 | Pin for Brush Holders | Pin for Brush Holders | 24 | [7 empty] | Cambridge | WL-1-EXS-BGR | 0
Brush carrier | Fastener | O-26763-002 | 11 | Castle nut for Clamping of Brush Gear | M24 Castle Nut, Plain Steel, Class 5 | 5 |  | Need details when in workshop? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Brush carrier | Fastener | O-26763-002 | 13 | Washer | 24mm Washer Extra Thick, Plain Steel | 5 |  | Need details when in workshop? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Brush carrier | Fastener | O-26763-002 | 14 | Hex screw for Brushgear | M16 x 35mm Hex Screw, Plain Steel, Class 5.6 | 12 |  | Changed length due to Nordlock | Y |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Brush carrier | Nordlock | O-26763-002 | 15 | Nordlock for Brushgear Screw | 16mm Nordlock Washer, Z/P | 12 |  | Change to Nordlock | Y |  |  | Y | Y | Tub 1 | WL-1-EXS-BGR | 0
Brush carrier | Fastener | O-26763-002 | 16 | Split pin for Castle Nut | 5 x 45mm Split Pin, Plain Steel | 5 | For item 11 | Need details when in workshop? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 1 | Rotor Lead - Conductor |  | 2 |  | Need Details (Pat)? | [5 empty] | ? | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 2 | Rotor Lead - Conductor |  | 2 |  | Need Details (Pat)? | [5 empty] | ? | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 3 | Rotor Lead - Conductor |  | 2 |  | Need Details (Pat)? | [5 empty] | ? | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 4 | Rotor Lead - Conductor |  | 2 |  | Need Details (Pat)? | [5 empty] | ? | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 5 | Reinforcement |  | 8 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 6 | Bushing |  | 2 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 7 | Bushing |  | 2 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 8 | Clamping piece |  | 2 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 10 | Clamping piece |  | 2 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 11 | Clamping piece |  | 2 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 12 | Clamping piece |  | 8 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 13 | Clamping piece |  | 8 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 14 | Clamping piece |  | 1 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 15 | Clamping piece |  | 1 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 16 | Conduit | Insulating Packing | 2 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-002 | 17 | Conduit | Insulating Packing | 8 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-003 | 18 | Conduit | Insulating Packing | 2 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-003 | 19 | Insulation |  |  |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-003 | 20 | Band |  |  |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-003 | 21 | Protective banding |  |  |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-003 | 22 | Bandage |  |  |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-003 | 26 | Clamping piece |  | 2 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for SR | Component | O-27134-003 | 27 | Clamping piece |  | 8 |  | Need Details (Pat)? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Connection for Slip Ring | Fastener | O-27134-003 | 29 | Hex bolt for Rotor Lead - Pole Connection | M20 x 80mm Hex Screw, Plain Steel, Class 5.6 | 2 |  |  | Y |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Fastener | O-27134-003 | 30 | Hex bolt for Rotor Lead - Pole Connection | M10 x 18mm Hex Screw, Plain Steel, Class 5.6 | 4 |  |  | Y |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Fastener | O-27134-003 | 31 | Hex bolt for Rotor Lead Insulation Block | M12 x 25mm Hex Screw, Plain Steel, Class 5.6 | 8 |  |  | Y |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Fastener | O-27134-003 | 32 | Hex bolt for Rotor Lead - Brush Gear Connection | M12 x 100mm Hex Bolt, Plain Steel, Class 5.6 | 2 | For item 1 |  | Y |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Fastener | O-27134-003 | 33 | Disc (Washer) for Rotor Lead -Brushgear Bolt | M12 x 13mm 5mm, plain steel | 2 | For item 32 |  | N |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Tab Washer | O-27134-003 | 34 | Locking plate | 14mm hole with 60mm centres | 1 | For item 32 |  | N | Site | Pat |  |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Tab Washer | O-27134-003 | 35 | Locking plate | M20 Din 93 | 2 | For item 29 | [6 empty] | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Tab Washer | O-27134-004 | 36 | Locking plate | M10 Din 93 | 2 | For item 37 | [6 empty] | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Fastener | O-27134-004 | 37 | Hex bolt for Rotor Lead - Brush Gear Connection | M10 x 40mm Hex Bolt, Plain Steel, Class 5.6 | 4 | For item 1 |  | Y |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Fastener | O-27134-004 | 38 | Hex Nut for Rotor Lead - Pole Connection Bolts | M10 Nut, Plain Steel, Class 5 | 12 | For item 30, 41 and 42 |  | Y |  |  | Y | Y | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Tab Washer | O-27134-004 | 39 | Locking plate | 11mm hole with 40mm centres | 4 |  |  | N | Site | Pat |  |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Fastener | O-27134-004 | 40 | Hex Bolt for Rotor Lead Connections | M10 x 24mm Hex Screw, Plain Steel, Class 5.6 | 4 |  |  | Y |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Fastener | O-27134-004 | 41 | Hex Bolt for Rotor Lead Connections | M10 x 32mm Hex Screw, Plain Steel, Class 5.6 | 4 |  |  | Y |  |  | Y |  | Tub 1 | WL-1-EXS-BGR | 0
Connection for Slip Ring | Tab Washer | O-27134-004 | 42 | Locking plate | 11mm hole with 30mm centres | 8 | For item 30 |  | N | Site | Pat |  |  | Tub 1 | WL-1-EXS-BGR | 0
Exciter support | Component | O-27292-002 | 1 | Exciter support |  | 1 | [7 empty] | TEC | WL-1-EXS-BGR | 0
Exciter support | Nordlock | O-27292-002 | 7 | Nordlock Washer for Labyrinth Pipe Screw | 12mm Nordlock Washer, Z/P | 4 | For item 12 | Changed with Nordlock | N |  |  | Y | Y | Tub 2 | WL-1-EXS-BGR | 0
Exciter support | Component | O-27292-002 | 8 | Cover for Exciter Support |  | 1 | [7 empty] | TEC | WL-1-EXS-BGR | 0
Exciter support | Fastener | O-27292-002 | 12 | Hex Screw for Labyrinth Pipe | M12 x 30mm Hex Screw, Plain Steel, Class 5.6 | 4 | For item 16 |  | N |  |  | Y |  | Tub 2 | WL-1-EXS-BGR | 0
Exciter support | Fastener | O-27292-002 | 13 | Countersunk Screw for Exciter Support Cover | M8 x 12mm, Plain Steel, Class 12.9 | 12 | For item 8 | Confirm if replaced with new design, Make sure countersunk suits allen head? | [5 empty] | N/A | WL-1-EXS-BGR | 0
Exciter support | Fastener | O-27292-002 | 14 | Hex Screw for Exciter Support | M20 x 50mm Hex Screw, Plain Steel, Class 5.6 | 12 |  | Changed length due to Nordlock | Y |  |  | Y |  | Tub 2 | WL-1-EXS-BGR | 0
Exciter support | Nordlock | O-27292-002 | N/A | Nordlock Washer for Exciter Support Screw | 20mm Nordlock Washer, Z/P | 12 | For item 14 |  | Y |  |  | Y | Y | Tub 2 | WL-1-EXS-BGR | 0
Exciter support | Component | O-27292-002 | 16 | Pipe for Labyrinth |  | 2 | [7 empty] | ? | WL-1-EXS-BGR | 0
PMG | Nordlock | O-27301 | 5 | Nordlock for PMG Winding Cover Bolts | 8mm Nordlock Washer, Z/P | 28 |  | Change to Nordlock | Y |  |  |  |  | N/A | WL-1-EXS-BGR | 0
PMG | Fastener | O-27301 | 6 | Hex Bolt for PMG Winding Cover | M8x15mm Hex bolt, Z/P, Class 5.6 | 28 |  | Confirm Quantity? | [5 empty] | N/A | WL-1-EXS-BGR | 0
PMG | Fastener | O-27298 | 4 | Hex Bolt for PMG Magnet Wheel | M20x50mm Hex Bolt, Z/P, Class 5.6 | 6 | [7 empty] | N/A | WL-1-EXS-BGR | 0
PMG | Tab Washer | O-27298 | 5 | Tab Washer for PMG Magnet Wheel Bolt | 20mm Din 432 Z/P | 6 | [7 empty] | Tub 2 | WL-1-EXS-BGR | 0

## Shaft Seal
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Shaft Seal Housing | Component | O-25849 | 49 | Shaft Seal Carbon Packing Housing | Shaft Seal Carbon Packing Housing | 1 |  |  | Y |  |  |  |  | Gowrie Park | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Seal | O-25849 | 4 | O-Ring for Shaft Seal Housing | 5mm, Shore 70 | 1 |  |  | Y | Site | Tom | Y |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Fastener | H16731 | 10 | Bolts for Shaft Seal Housing | M20 x 50mm Hex Head Bolt, Z/P, Class 8.8 | 16 | For item 49 on drawing O-25849 |  | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Nordlock | H16731 | N/A | Nordlocks for Carbon Packing Housing Bolts | 20mm Nordlock Washers, Z/P | 16 | For item 49 on drawing O-25852 |  | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Fastener | H16731 | 11 | Bolts for Shaft Seal Housing Joint | M12 x 60mm Hex Head Bolt, Z/P, Class 8.8 | 6 | For item 49 on drawing O-25850 |  | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Fastener | H16731 | 9 | Nuts for Shaft Seal Housing Joint Bolts | M12, Z/P, Class 8 | 6 | For item 49 on drawing O-25851 |  | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Nordlock | H16731 | N/A | Nordlocks for Shaft Seal Housing Joint Bolts | 12mm Nordlock Washers, Z/P | 12 | For item 49 on drawing O-25852 |  | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Component | H16732 | 8 | Fitted Bolts for Shaft Seal Housing Joint | M12 x 60mm, plain steel, machined to suit | 4 | For item 49 on drawing O-25853 |  | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Fastener | H16733 | 9 | Nuts for Shaft Seal Housing Joint Fitted Bolts | 12mm Nordlock Washers, Z/P | 4 | For item 49 on drawing O-25854 |  | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Nordlock | H16734 | N/A | Nordlocks for Shaft Seal Housing Joint Fitted Bolts | 12mm Nordlock Washers, Z/P | 8 | For item 49 on drawing O-25855 |  | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Nordlock | H16731 | 16 | Dowels for Housing Joint | 10mm Parrallel pin | 2 | For item 49 on drawing O-25855 |  | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Shaft Seal Housing | Dowel | H16731 | 13 | Dowels for Shaft Seal Housing | 20mm x 50mm, 4140 | 2 | For item 49 on drawing O-25856 | New Parrallel? | Y |  |  |  |  | Tub 1 | WL-1-TUR-SHT-SEA | 0
Sliding Plate | Component | O-25849 | 46 | Sliding Plate | Sliding Plate for Shaft Seal | 1 |  |  | Y |  |  |  |  | Installed | WL-1-TUR-SHT-SEA | 0
Sliding Plate | Fastener | O-27718 | N/A | Capscrews for Sliding Plate | M16 x 25mm? SH Capscrew, Class C3-80 | 28 | For item 46 |  | N | Voith | Matt/Tom |  |  | Installed | WL-1-TUR-SHT-SEA | 0
Sliding Plate | Fastener | O-27718 | N/A | Scotch Keys for Sliding Plate Capscrews | M5 x 8mm Blind Set Screw, Socket Head, Class A2-50 | 28 |  |  | N |  |  |  |  | Installed | WL-1-TUR-SHT-SEA | 0
Packing Cover | Component | O-25849 | 50 | Carbon Packing Cover | Packing Cover for Shaft Seal | 1 |  |  | Y |  |  |  |  | Gowrie Park | WL-1-TUR-SHT-SEA | 0
Packing Cover | Fastener | H203935 | 11 | Bolts for Packing Cover | M12 x 25mm Hex Head Bolt, Z/P, Class 8.8 | 16 |  |  | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Packing Cover | Nordlock | H203935 | N/A | Nordlocks for Packing Cover Bolts | 12mm Nordlock Washers, Z/P | 16 | For item 11 | Do We need these? | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Packing Cover | Fastener | H203935 | 12 | Bolts for Packing Cover Joint | M12 x 45mm Hex Head Bolt, Z/P, Class 8.8 | 4 |  |  | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Packing Cover | Fastener | H203935 | 13 | Nuts for Packing Cover Joint Bolts | M12, Z/P, Class 8 | 4 |  |  | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Packing Cover | Nordlock | H203935 | N/A | Nordlocks for Packing Cover Joint Bolts | 12mm Nordlock Washers, Z/P | 8 | For item 12 and 13 | Do We need these? | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Packing Cover | Seal | H16731 | 17 | O-Ring for Packing Cover | 5mm, Shore 70 | 1 |  |  | Y | Site | Tom | Y |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Packing Cover | Dowel | H203935 | 4 | Dowels for Packing Cover Joint | 10mm taper dowel | 2 |  | Confirm Details? | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Wear Indicator | Component | H528391 | 1 | Indicator Rod | Indicator Rod | 1 |  |  | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Wear Indicator | Component | H534611 | 1 | Lever | Lever | 1 |  |  | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Wear Indicator | Fastener | H534611 | 2 | Screw for Lever | M8 x 20mm Hex Head Bolt, Z/P, Class 8.8 | 2 |  |  | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Wear Indicator | Nordlock | H534611 | 3 | Nordlocks for Lever | 8mm Nordlock Washers, Z/P | 2 | For Lever |  | Y |  |  |  |  | Tub 2 | WL-1-TUR-SHT-SEA | 0
Wear Indicator | Component | O-27673 | N/A | Stopper | Stopper | 1 |  |  | Y |  |  |  |  | Gowrie Park | WL-1-TUR-SHT-SEA | 0
Wear Indicator | Fastener | O-27673 | N/A | Screw for Stopper | M8 x 20mm Hex Head Bolt, Z/P, Class 8.8 | 16 |  |  | Y |  |  |  |  | Tub 3 | WL-1-TUR-SHT-SEA | 0
Wear Indicator | Nordlock | O-27673 | N/A | Nordlocks for Stopper | 8mm Nordlock Washers, Z/P | 16 | For Stopper |  | Y |  |  |  |  | Tub 3 | WL-1-TUR-SHT-SEA | 0
Carbon Ring Holder | Component | O-25849 | 47 | Carbon Rings | Carbon | 2 | Glued in Item 48 |  | Y |  |  |  |  | Installed | WL-1-TUR-SHT-SEA | TBC
Carbon Ring Holder | Component | O-25849 | 48 | Carbon Ring Holder | Carbon Ring Holder | 1 |  |  | Y |  |  |  |  | Gowrie Park | WL-1-TUR-SHT-SEA | 0
Carbon Ring Holder | Seal | H203934 | 52 | O-Rings for Carbon Ring Holder | 8mm, 70 Shore | 2 |  |  | Y | Site | Tom | Y |  | Tub 3 | WL-1-TUR-SHT-SEA | 0
Carbon Ring Holder | Fastener | H203934 | 7 | Top Capscrews for Carbon Ring Holder | M10 x 35mm SH Capscrew, Z/P, Class 12.9 | 2 |  |  | Y |  |  |  |  | Gowrie Park | WL-1-TUR-SHT-SEA | 0
Carbon Ring Holder | Nordlock | H203934 | N/A | Nordlocks for Carbon Ring Holder Top Capscrews | 10mm Nordlock Washers, Z/P | 2 |  | Do We need these? | Y |  |  |  |  | Gowrie Park | WL-1-TUR-SHT-SEA | 0
Carbon Ring Holder | Fastener | H203934 | 6 | Bottom Capscrews for Carbon Ring Holder | M20 x 45mm SH Capscrew, Z/P, Class 12.9 | 2 |  |  | Y |  |  |  |  | Gowrie Park | WL-1-TUR-SHT-SEA | 0
Carbon Ring Holder | Nordlock | H203934 | N/A | Nordlocks for Carbon Ring Holder Bottom Capscrews | 20mm Nordlock Washers, Z/P | 2 |  | Do We need these? | Y |  |  |  |  | Gowrie Park | WL-1-TUR-SHT-SEA | 0
Carbon Ring Holder | Dowel | H203934 | 8 | Guide Pins for Carbon Ring Holder | 16mm x 80mm | 2 |  | Confirm Details? | Y |  |  |  |  | Tub 3 | WL-1-TUR-SHT-SEA | 0
Carbon Ring Holder | Component | O-27673 | 16 | Springs for Carbon Ring Holder | O-60305 | 16 |  | Confirm Details? | Y |  |  |  |  | Tub 3 | WL-1-TUR-SHT-SEA | 16
Carbon Ring Holder | Component | O-25849 | N/A | Glue for Carbon Rings | Araldite Huntsman 2014-2 | 1 | [8 empty] | WL-1-TUR-SHT-SEA | 1

## Other Components
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2020-01-31
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Cooling Water Pump | Component | O-60741-002 | 1 | Electric Motor | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 2 | Coupling | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 3 | Shaft Key - Coupling | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 4 | Motor Stool Seal | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 5 | Motor Stool Bearing | NSK 6307C3 or NSK 6307VVC3E | [9 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Seal | O-60741-002 | 6 | Motor Stool Bearing O-Ring | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 2
Cooling Water Pump | Component | O-60741-002 | 8 | Column Filler Plug | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 9 | Shaft Key | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 10 | Intermediate Bearing Bush | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 11 | Intermediate Bearing Holder | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Seal | O-60741-002 | 12 | Intermediate Bearing O-Ring | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 13 | Shaft Collar | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 14 | Bottom Bearing | NSK 6307C3 or NSK 6307VVC3E | [9 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 15 | Back Plate | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Seal | O-60741-002 | 16 | Secondary Mechanical Seal | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 17 | Circlip | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Seal | O-60741-002 | 18 | Primary Seal | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 19 | Back Cover | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 20 | Impeller Key | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 21 | Impeller | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 22 | Impeller Nut | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 23 | Casing Wear Ring | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Seal | O-60741-002 | 24 | Casing O-Ring | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | TBC
Cooling Water Pump | Component | O-60741-002 | 25 | Casing | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 1
Cooling Water Pump | Component | O-60741-002 | 26 | Strainer | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 27 | Riser Pipe | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 28 | Casing Gasket | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 29 | Oil Line | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Component | O-60741-002 | 30 | Oil Filler & Sight Glass | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2
Cooling Water Pump | Seal | O-60741-002 | 31 | Bottom Bearing O-Ring | [10 empty] | WL-1-CWS-PS1, WL-1-CWS-PS2 | 2
Regulating Ring | Component | O-60601 | N/A | Axial Bearing Strip | Regulating Ring Axial Bearing Strip, DU Bearing 160x30x3 | 18 | Supplied with mandrel punch | [7 empty] | WL-1-TUR-RGS | 18
Regulating Ring | Component | O-60594 | N/A | Radial Bearing Strip | Regulating Ring Radial Bearing Strip, DU Bearing 500x70x3 | 6 | Supplied with mandrel punch | [7 empty] | WL-1-TUR-RGS | 6
Regulating Ring | Component | O-28157 | 14 | Regulating Mechanism Thrust Liner | O-28160 Regulating Mechanism Thrust Liner - DU Dry Bearing (two halves) | 1 | [8 empty] | WL-1-TUR-RGS | 1
Generator Pit Cover | Seal | O-26996 | 15 | Floor Plate Seal | Seal inbetween 4 floor plates | 4 | [8 empty] | WL-1-ALT | ~10m
Generator Pit Cover | Seal | O-26996 | 16 | Floor Plate Seal | Seal inbetween inside diameter of floor plates and thrust bracket oil pot | 10m | [8 empty] | WL-1-ALT | ~10m
Guide Vane Servomotor | Seal | O-25570 | 22 | Rod Seal | SKF Rod Seal ID135 OD165 H16 | 1 | [8 empty] | WL-1-TUR-RGS-ACT | 1
Guide Vane Servomotor | Seal | O-25570 | 25 | O-Ring Vulcanised | O-Ring Vulcanised 410x7 - Endcaps to body | 2 | [8 empty] | WL-1-TUR-RGS-ACT | 2
Distributing Valve | Seal | A1-16120 | 29 | O-Ring P16 | O-Ring P16 Duro 70 (15.8 x 2.4) | 2 | [8 empty] | WL-1-GOV-CTE | 2
Distributing Valve | Seal | A1-16120 | 44 | O-Ring G150 | O-Ring G150 Duro 70 (149.3x5.7) | 5 | [8 empty] | WL-1-GOV-CTE | 6
Distributing Valve | Seal | A1-16120 | 43 | O-Ring P110 | O-Ring P110 Duro 70 (109.6x5.7) | 1 | [8 empty] | WL-1-GOV-CTE | 1
Alternator Water Spray | Components | N/A | N/A | Fittings Misc | AWS Fittings Misc | 1 | [8 empty] | WL-1-ALT-FDS | 1
Alternator Water Spray | Components | N/A | N/A | Hose | AWS Hose | 1 | [8 empty] | WL-1-ALT-FDS | 1
Governor Hydraulic | Components | O-60737 | N/A | Governor Accumulator PRV | Set to 2440kPa | 1 | [8 empty] | WL-1-GOV-HYD-PV1-SV1 | 1
Governor Air Compressor | Components | O-60624 |  | Air Filter Element | Ingersol Rand part no 32170979 | 1 | [8 empty] | WL-S-CAS-CP1 | 1

## Main Inlet Valve
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Inlet Valve | Component | O-25549 | 1 | Valve body (upstream side) | Valve body (upstream side) | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 2 | Valve body (downstream side) | Valve body (downstream side) | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 3 | Rotating valve |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 4 | Trunnion |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 5 | Trunnion (thrust bearing side) |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Bearing | O-25549 | 6 | Main bearing bush |  | 2 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 7 | Packing retainer (thrust bearing side) |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Seal | O-25549 | 8 | V Type rubber packing | 10K Rod Mount. 340x380x25 NBR-85. See Drawing No.O-60689 | 2 |  | Need to confirm type, size, dimensions etc.? | N | Cambridge | Glenn |  |  |  | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 9 | Packing holder |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Bearing | O-25549 | 10 | Thrust bearing |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 11 | Thrust bearing holder |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 12 | Downstream distance plate |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 13 | Sleeve |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 14 | Follower ring |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Seal | O-25549 | 15 | Oring Dismantling Joint Follower Ring | 12mm, 70 shore | 1 |  | Need to confirm type, size, dimensions etc.? | N | Cambridge | Glenn |  |  |  | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 16 | Flange |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 17 | Downstream seat ring |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 18 | Downstream seating rubber holder |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Seal | O-25549 | 19 | Downstream seating rubber | CANCELLED | 1 |  | No longer required, metal/metal seal. Arrangment drawing updated | N | Cambridge | Glenn |  |  |  | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 20 | Upstream distance plate |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 21 | Upstream seat ring |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 22 | Upstream seating rubber holder |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Seal | O-25549 | 23 | Upstream seating rubber | CANCELLED | 1 |  | No longer required, metal/metal seal. Arrangment drawing updated | N | Cambridge | Glenn |  |  |  | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 24 | Lever |  | ? | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 25 | Pin (lever side) | 120 f7 x 330mm. See Drawing O-60687 | 2 |  | Supplied with replacement servomotors | Y | Cambridge | Glenn |  |  |  | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 26 | Pin (piston side) |  | 2 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 27 | Bearing bush (lever side) |  | 2 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 28 | Bearing bush (piston side) |  | 2 | [7 empty] | N/A | WL-1-MIV | 0
Servomotor | Component | O-25549 | 29 | Connecting rod |  | 2 |  | RELATES TO OLD SERVOMOTOR NOT RELEVANT | [5 empty] | N/A | WL-1-MIV | 0
Servomotor | Component | O-25549 | 30 | Piston |  | 2 |  | RELATES TO OLD SERVOMOTOR NOT RELEVANT | [5 empty] | N/A | WL-1-MIV | 0
Servomotor | Component | O-25549 | 31 | Piston bush |  | 2 |  | RELATES TO OLD SERVOMOTOR NOT RELEVANT | [5 empty] | N/A | WL-1-MIV | 0
Servomotor | Component | O-25549 | 35 | Cylinder |  | 2 |  | RELATES TO OLD SERVOMOTOR NOT RELEVANT | [5 empty] | N/A | WL-1-MIV | 0
Servomotor | Component | O-25549 | 38 | Upper cylinder cover |  | 2 |  | RELATES TO OLD SERVOMOTOR NOT RELEVANT | [5 empty] | N/A | WL-1-MIV | 0
Servomotor | Bearing | O-25549 | 39 | Bearing bush |  | 2 |  | RELATES TO OLD SERVOMOTOR NOT RELEVANT | [5 empty] | N/A | WL-1-MIV | 0
Servomotor | Component | O-25549 | 40 | Lower cylinder cover |  | 2 |  | RELATES TO OLD SERVOMOTOR NOT RELEVANT | [5 empty] | N/A | WL-1-MIV | 0
Servomotor | Component | O-25549 | 41 | Mounting plate for servomotor |  | 2 |  | RELATES TO OLD SERVOMOTOR NOT RELEVANT | [5 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 42 | Lock plate |  | 2 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 42 | Hex Bolts for Lock plate | M16 x 35mm, Plain Steel, Grade? | 4 |  | For item 42 | Y | Site | Tom |  |  |  | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 43 | Tangential key |  | 4 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 44 | Locking pin |  | ? | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 45 | Key |  | ? | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 46 | Bush |  | ? | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 47 | Bush |  | ? | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 48 | Cover |  | ? | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 49 | Key |  | 8 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 50 | Packing retainer |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 51 | Plug |  | 4 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 52 | Packing holder |  | 4 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 53 | Extension piece of penstock |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 54 | Lever |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 55 | Mounting plate for valve body |  | 2 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | 56 | Lock bolts of upstream seal | M36x4. 197mm Long | 12 |  | To be re-used - Cambridge to NDT, paint etc | N | Cambridge | Glenn |  |  |  | WL-1-MIV | 0
Inlet Valve | Bearing | O-25549 | 57 | Bush | 340mmx380mmx25mm from NBR-85 | 12 |  | For item 36 | [5 empty] | N/A | WL-1-MIV | 0
Position Indicator | Component | O-25549 | 58 | Control rod | For Service Seal Positon Indicator Assemblies | 1 |  | Are these re-used? Assembled with 1 x item 66 | Y | Site | Tom |  |  |  | WL-1-MIV | 0
Inlet Valve | Bearing | O-25549 | 59 | Bush |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Position Indicator | Bearing | O-25549 | 60 | Bush | For Service Seal Positon Indicator Assemblies | 1 |  | Are these re-used? Assembled with 1 x item 66 | Y | Site | Tom |  |  |  | WL-1-MIV | 0
Position Indicator | Component | O-25549 | 61 | O-Ring for Control Rod | 2.4 mm x ?? | 1 |  | Fitted in Inlet Valve | N | Site | Tom |  |  |  | WL-1-MIV | 0
Position Indicator | Component | O-25549 | 61 | Indicating needle | For Service Seal and Maintence Seal Positon Indicator Assemblies | 4 |  | Are these re-used? Assembled with 4 x item 66 | Y | Site | Tom |  |  |  | WL-1-MIV | 0
Position Indicator | Component | O-25549 | 61 | O-Ring for Indicating needle | 2.4 mm x ?? | 4 |  | Fitted in Inlet Valve | N | Site | Tom |  |  |  | WL-1-MIV | 0
Position Indicator | Bearing | O-25549 | 62 | Bush | For Service Seal and Maintence Seal Positon Indicator Assemblies | 4 |  | Are these re-used? Assembled with 4 x item 66 | Y | Site | Tom |  |  |  | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 63 | Stopper | ? | ? |  | not supplied to workshop | N | Site | Tom |  |  |  | WL-1-MIV | 0
Inlet Valve | Component | O-25549 | 64 | Scour valve | ? | 1 |  | not supplied to workshop | N | Site | Tom |  |  |  | WL-1-MIV | 0
Position Indicator | Component | O-25549 | 65 | Spring | For Service Seal and Maintence Seal Positon Indicator Assemblies | 5 |  | Are these re-used? Assembled with 4 x item 66 | Y | Site | Tom |  |  |  | WL-1-MIV | 0
Position Indicator | Component | O-25549 | 66 | Spring case | For Service Seal and Maintence Seal Positon Indicator Assemblies | 5 |  | Are these re-used? Assembled with 4 x item 66 | Y | Site | Tom |  |  |  | WL-1-MIV | 0
Inlet Valve | Bearing | O-25549 | 67 | Bush |  | 1 | [7 empty] | N/A | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | 68 | Stud for Inlet Valve to Penstock | M40x2 x 250, AS1444 4140 Cond T. See Drawing A1-16093 | 36 |  |  | Y | Cambridge | Glenn | Y |  |  | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | 68 | Nut for Inlet Valve to Penstock | M40x2, AS1444 4140 Cond T.See Drawing A1-16093 | 36 |  |  | Y | Cambridge | Glenn | Y |  |  | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | 69 | Stud for MIV Body | M48x2 x 220, AS1444 4140 Cond T.See Drawing A1-16093 | 48 |  |  | N | Cambridge | Glenn | Y |  |  | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | 69 | Nut for MIV Body | M48x2, AS1444 4140 Cond T.See Drawing A1-16093 | 48 |  |  | N | Cambridge | Glenn | Y |  |  | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | 70 | Hex Bolt For Dismantling Ring to Inlet Valve | M45x2 x 180, AS1444 4140 Cond T.See Drawing A1-16093 | 36 |  |  | Y | Cambridge | Glenn | Y |  |  | WL-1-MIV | 0
Inlet Valve | Seal | O-25549 | N/A | Oring Penstock to Inlet Valve | 7mm, 70 Shore? | 1 |  | Need to confirm type, size, dimensions etc.? | N | Site | Tom |  |  |  | WL-1-MIV | 0
Inlet Valve | Seal | O-25549 | N/A | Oring Spiral to Dismantling Ring | 7mm, 70 Shore? | 1 |  | Need to confirm type, size, dimensions etc.? | N | Site | Tom |  |  |  | WL-1-MIV | 0
Inlet Valve | Seal | O-25549 | N/A | Oring Dismantling Ring to Spiral | 7mm, 70 Shore? | 1 |  | Is this a double up of above | N | Cambridge | Matt/Glenn |  |  |  | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | N/A | Studs for Dismanlting Ring to Spiral Casing | M40x2 x 220, AS1444 4140 Cond T. See Drawing A1-16093 | 36 |  |  | Y | Cambridge | Glenn | Y |  |  | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | N/A | Nuts for Dismanlting Ring to Spiral Casing | M40x2, AS1444 4140 Cond T.See Drawing A1-16093 | 72 |  |  | Y | Cambridge | Glenn | Y |  |  | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | N/A | Follower Ring to Dismantling Ring Bolts | M16 X 55mm, Z/P, Grade 8.8 | 36 |  |  | Y | Cambridge | Glenn |  |  |  | WL-1-MIV | 0
Inlet Valve | Fastener | O-25549 | N/A | MIV Foot Bolts | M42x2 x 120, AS1444 4140 Cond T. See Drawing A1-16093 | 8 |  | These have been ordered by Cambridge. M42 x 120 Long See drawing A1-16093 | Y | Cambridge | Glenn |  |  |  | WL-1-MIV | 0
Inlet Valve | Dowels | O-25549 | N/A | MIV Foot Dowels | ? | 2 |  | Check Sizes with Hally? | N | Site | Jeremy |  |  |  | WL-1-MIV | 0
Inlet Valve | Dowels | O-25549 | N/A | Inlet Valve to Dismantling Ring Dowels | ? | 4 |  | Check Sizes with Hally? | N | Site | Jeremy |  |  |  | WL-1-MIV | 0
Inlet Valve | Dowels | O-25549 | N/A | Inlet Valve to Penstock Dowels | ? | 4 |  | Check Sizes with Hally? | N | Site | Jeremy |  |  |  | WL-1-MIV | 0
Servomotor | Fastener | O-25549 | N/A | Servomotor Hold Down Studs | M36 x 170mm, Plain Steel, S35C? | 32 |  | Confirm if re-used? If so grade size etc? | Y | Site | Tom |  |  |  | WL-1-MIV | 0
Servomotor | Fastener | O-25549 | N/A | Servomotor Hold Down Nuts | M36, Plain Steel, S25C? | 32 |  | Confirm if re-used? If so grade size etc? | Y | Site | Tom |  |  |  | WL-1-MIV | 0
Servomotor | Dowels | O-25549 | N/A | Servomotor Dowels | ? | 4 |  | Check Sizes with Hally? | N | Site | Jeremy |  |  |  | WL-1-MIV | 0
Bypass Valve | Seal | O-25957 | 38 | Packing | Copper Washer? | 1 |  | Need to confirm type, size, dimensions etc.? | N | Site | Tom |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Fastener | O-25957 | N/A | Bypass to Spool Piece Bolts | M20 x 130mm, S45C? | 8 |  | Need to confirm Grade? | Y | Site | Tom |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Fastener | O-25957 | N/A | Bypass to Spool Piece Nuts | M20, S35C? | 8 |  | Need to confirm Grade? | Y | Site | Tom |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Fastener | O-25957 | N/A | Bypass to Spiral Stub Bolts | M20 x ??mm, S45C? | 8 |  | Need to confirm Size, Length, Grade, Coating etc.? | N | Site | Tom |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Fastener | O-25957 | N/A | Bypass to Spiral Stub Nuts | M20, S35C? | 8 |  | Need to confirm Size, Length, Grade, Coating etc.? | N | Site | Tom |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Seal | O-25957 | N/A | Bypass to Spiral Stub O-Ring | 6mm, 70 Shore? | 1 |  | Need to confirm type, size, dimensions etc.? | N | Site | Tom |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Seal | O-60584 |  | V-Type Rubber Packing | ? | 2 |  | Check with Tom as I think he may have updated this with new BPV. If he hasn't let me know. | N | Cambridge | Glenn |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Seal | O-60584 |  | V-Type Rubber Packing | ? | 2 |  | Check with Tom as I think he may have updated this with new BPV. If he hasn't let me know. | N | Cambridge | Glenn |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Seal | O-60584 |  | Oring for Piston to Valve Rod | 3.2mm x 32mm, 70 Shore? | 2 |  | Check with Tom as I think he may have updated this with new BPV. If he hasn't let me know. | N | Cambridge | Glenn |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Seal | O-60584 |  | V-Type Rubber Packing | ? | 1 |  | Check with Tom as I think he may have updated this with new BPV. If he hasn't let me know. | N | Cambridge | Glenn |  |  |  | WL-1-MIV-BV1 | 0
Bypass Valve | Seal | O-60584 |  | Oil Seal Packing | ? | 1 |  | Check with Tom as I think he may have updated this with new BPV. If he hasn't let me know. | N | Cambridge | Glenn |  |  |  | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 1 | Body | 0 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 1.1 | Flange | Flange S355J2+N | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 1.2 | Flange | Flange S355J2+N | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 1.3 | Sleeve | Sleeve S355J2+N | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 1.4 | Arrow | Arrow S355J2+N | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 2 | Throttling Plate | Throttling Plate See A1-16265, 420 Stainless Steel | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 3 | Sealing Ring | Sealing Ring 1.4301 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 4 | Spindle | Spindle 1.4313 QT780 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 5 | Valve head | Valve head 1.4418 QT900 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 7 | Cover | Cover 1.4418 QT900 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 8.1 | Flange | Flange 1.4418 QT900 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 8.2 | Pipe | Pipe 1.4301 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 8.3 | Flange | Flange 1.4418 QT900 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 10 | Piston | Piston 1.4301 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 11 | Rod | Rod 1.4021 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 12.1 | Console 1 | Console 1 1.4021/1.4301 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 12.2 | Console 2 | Console 2 1.4021/1.4301 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 13 | Plate | Plate 1.4021/1.4301 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 14 | Orifice | Orifice 1.4301 | 6 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 15 | Bracket | Bracket 1.4021/1.4301 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 16 | End Stop | End Stop 1.4021/1.4301 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 60.08 | Threaded Rod | Threaded Rod A2-70 | 8 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.02 | Socket Head Screw | Socket Head Screw DIN 912 A2-70 | 8 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.04 | Nut | Nut DIN 934 A2 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.05 | Socket Head Screw | Socket Head Screw DIN 915 A2/A4 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.07 | Socket Head Screw | Socket Head Screw DIN 912 A2-70 | 6 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.08 | Hexagon Screw | Hexagon Screw DIN 933 A2-70 | 8 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.1 | Socket Head Screw | Socket Head Screw DIN 915 A2/A4 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.11 | Hexagon Screw | Hexagon Screw DIN 933 A2-70 | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.15 | Hexagon Screw | Hexagon Screw DIN 933 A2/A4 | 2 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.6 | Nut | Nut DIN 934 A2-70 | 16 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.02 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=183.52 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.03 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=142.24 | 2 | [8 empty] | WL-1-MIV-BV1 | 2 (TBC)
MIV Bypass Valve | Component | O-60584-002 | 90.1 | Limit Switches | Limit Switch Telemecanique XS612B1PAM12 | 2 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 90.2 | Connector | Connector Schneider Electric XZCC 12FCM40B | 2 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 100 | Name Plate | Name Plate | 1 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.12.1 | Hexagon Screw | Hexagon Screw DIN 933 A2/A4 | 4 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Fastener | O-60584-002 | 80.12.2 | Nut | Nut DIN 934 A2/A4 | 2 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Seal | O-60584-002 | 83.07.01 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=59.69 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.07.02 | Guide Ring | Guide Ring PTFE + Bronze, Ø40 x Ø43 x 5.6 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.07.03 | Groove Ring | Groove Ring Polyurethane Ø40 x Ø60 BL=11 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.08.01 | Groove Ring | Groove Ring Polyurethane Ø40 x Ø60 BL=11 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.08.02 | Guide Ring | Guide Ring PTFE + Bronze, Ø40 x Ø43 x 5.6 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.08.03 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=100.97 | 2 | [8 empty] | WL-1-MIV-BV1 | 2 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.08.04 | Groove Ring | Groove Ring Polyurethane Ø40 x Ø60 BL=11 | 2 | [8 empty] | WL-1-MIV-BV1 | 2 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.08.05 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=148.59 | 2 | [8 empty] | WL-1-MIV-BV1 | 2 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.08.06 | Groove Ring | Groove Ring Polyurethane Ø20 x Ø30 BL=6 | 2 | [8 empty] | WL-1-MIV-BV1 | 2 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.08.07 | Guide Ring | Guide Ring PTFE + Bronze, Ø20 x Ø23 x 4 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.08.08 | Wiper Seal | Wiper Polyurethane Ø20 x Ø28 #4/7 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.10.1 | Piston Seal | Piston Seal NBR + POM + Polyester Ø160 x Ø130 x 25.4/12.7 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Seal | O-60584-002 | 83.10.2 | O-Ring | O-Ring NBR Duro 70, Ø5.33 ID=37.47 | 1 | [8 empty] | WL-1-MIV-BV1 | 1 (TBC)
MIV Bypass Valve | Component | O-60584-002 | 86.08.1 | Plug | Plug DIN 3852 Stainless Steel | 3 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Bypass Valve | Component | O-60584-002 | 86.08.2 | Test Coupling | Test Coupling Stainless Steel | 2 | [8 empty] | WL-1-MIV-BV1 | 0
MIV Servomotor | Component | A1-16274 |  | Flexible Hose Ferrule | Ferrule, SS Pegasus Hydraulics P/N P1-DN 31 | 8 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 8
MIV Servomotor | Component | A1-16274 |  | Flexible Hose Hose Tail 90 Degree | SAE Code 61 Flanged Insert 90 Degree, SS, Pegasus Hydraulics P/N SFL3-1 1/4"-DN 31 | 8 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 4 On order
MIV Servomotor | Component | A1-16274 |  | Flexible Hose Hose Tail | SAE Code 61 Flanged Insert, SS, Pegasus Hydraulics P/N SFL3-1 1/4"-DN 31 | 8 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 4
MIV Servomotor | Component | O-60687-001 | 4066464 | Clevis Bush | CuSn7Zn4Pb7 Bush | 4 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2
MIV Servomotor | Component | O-60687-001 | 4066466 | Clevis Adjustment Ring | Clevis Adjustment Ring, Stainless Steel 17-4 PH | 2 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2
MIV Servomotor | Component | O-60687-001 | 4066585 | Anti-slam orifice blank | M30x2 SS Blank Orifice | 2 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2
MIV Servomotor | Seal | O-60687-001 | 01 | Rod Seal | Rod Seal ø480 (OD) | 4 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2
MIV Servomotor | Bearing | O-60687-001 | 02 | Guide Ring | Guide Ring - Hallite Type 506, 25 x 4 x Ø485OD | 4 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2
MIV Servomotor | Seal | O-60687-001 | 03 | Rod Seal | Rod Seal, Two Piece, Ø115ID | 2 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 1
MIV Servomotor | Seal | O-60687-001 | 04 | Lip Seal | Lip Seal, Ø115ID | 2 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 1
MIV Servomotor | Bearing | O-60687-001 | 05 | Guide Ring | Guide Ring - Hallite Type 506, 25 x 4 x Ø115OD | 2 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 1
MIV Servomotor | Seal | O-60687-001 | 06 | O-Ring | O-Ring | 4 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2
MIV Servomotor | Seal | O-60687-001 | 07 | O-Ring | O-Ring, Ø485ID | 2 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2
MIV Servomotor | Seal | O-60687-001 | 08 | O-Ring | O-Ring, Ø5.33x115ID | 4 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2
MIV Servomotor | Seal | O-60687-001 | 08 | O-Ring | O-Ring, Ø5.33x115ID | 2 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2
MIV Servomotor | Component | O-60687-002 | 4066470 | Stroke Adjustment Ring | Stroke Adjustment Ring, Stainless Steel AISI 316L | 2 |  | Qty total for both servomotors | [6 empty] | WL-1-MIV-ACT | 2

## Relief Valve
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Relief Valve | Component | O-25572 | 1 | Valve body |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 2 | Servomotor cylinder |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 3 | Bush |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 4 | Seal packing | No Details? | 1 |  | Need to confirm what this is? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 5 | Packing holder |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 6 | Piston |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Fastener | O-25572 | 7 | Nut | ? | 1 |  | Need to confirm size, coating, grade? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 8 | O-ring packing | 5.7mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 9 | Valve stem |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 10 | O-ring packing | 3.4mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 11 | Bush |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 12 | Bearing |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 13 | Bush |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 14 | Stopper |  | 2? | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 15 | Valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 16 | Valve seat (valve side) |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 17 | Valve seat (valve body side) |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 18 | Round rubber packing | 7mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Site | Tom |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 19 | Rod |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 20 | O-ring packing | 3.5mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 21 | Bush |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 22 | Cover |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 23 | Round rubber packing | 7mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 24 | Restoring cam |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 25 | Pin |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 26 | Restoring lever |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 27 | Cylinder for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 28 | Key for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Fastener | O-25572 | 29 | Nut for Dash Pot | ? | 1 |  | Need to confirm size, coating, grade? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 30 | Spring for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 31 | Guide for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 32 | Piston for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 33 | Piston rod for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 34 | Cover for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 35 | Frame for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 36 | for Dash PotCover |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 37 | Counter weight for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 38 | Floating lever for Dash Pot |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 39 | Rod for Regulating mechanism |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 40 | Link for Regulating mechanism |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 41 | Lever for Regulating mechanism |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 42 | Frame for Regulating mechanism |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 43 | Stopper |  | 2 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 44 | Pilot valve for Control valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 45 | Bush for Control valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 46 | Floating valve for Control valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 47 | Cover for Control valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 48 | Bush for Control valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 49 | Casing for Control valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 50 | Motorised gate valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 51 | Branch pipe |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 52 | Hand operated gate valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 53 | Bend pipe |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 54 | Oil seal |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 55 | Round rubber packing | 5mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 56 | Extension piece of branch pipe |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 57 | Bellow |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 58 | Rod |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 59 | Lever |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 60 | Stem |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 61 | Valve cover |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 62 | Valve casing |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 63 | Bush |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 64 | Pipe |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Fastener | O-25572 | 65 | Bolt for TRV to Outlet Flange | M30 x 80, Plain Steel, S25C M30 x 125, Plain Steel, S25C | 24? |  | These have been ordered and and to be replaced with studs, if site wanted to use Unknown to me however were the tapped holes. Will order a further 6 bolts to allow for these. Note the studs have been manufactured out of 4140 with a 2mm pitch as per other interface fasteners. The tapped holes are standard M30 coarse. | Y | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Fastener | O-25572 | 66 | Nut for TRV to Outlet Flange | M30, SS41 | ? |  | Need to confirm grade? | Y | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 67 | Round rubber packing | 7mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 68 | O-ring | 2.4mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 69 | Bend pipe |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 70 | Hand operated gate valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 71 | Mount for air valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 72 | Air valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 73 | Motorised gate valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 74 | Hand operated gate valve |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 75 | Shaft |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 76 | Round rubber packing | 6mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Seal | O-25572 | 77 | Round rubber packing | 5mm, Shore? | 1 |  | Need to confirm Shore and Dimensions? | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Component | O-25572 | 78 | Bend pipe |  | 1 | [7 empty] | N/A | WL-1-RVV | 0
Relief Valve | Fastener | O-25573 | N/A | Stud for TRV to Inlet Flange | M40? | ? |  | Need to confirm length, coating, grade? Drawing has not part number listed | N | Cambridge | Glenn |  |  |  | WL-1-RVV | 0
Relief Valve | Fastener | O-25574 | N/A | Nut for TRV to Inlet Flange | M40? | ? |  | Need to confirm coating, grade? Drawing has not part number listed | Y | Cambridge | Glenn |  |  |  | WL-1-RVV | 0

## Stator
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Stator Frame Machined | Component | O-59724 | 1 | STATOR FRAME WELDED | Refer to O-59725 (300865113) for welded assembly | 1 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Component | O-59724 | 2 | STEEL PLATE |  | 4 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Component | O-59724 | 3 | SHEET |  | 40 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Component | O-59724 | 4 | SHEET |  | 24 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Component | O-59724 | 5 | LEG ANGLE |  | 8 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Component | O-59724 | 6 | Leg Angle |  | 8 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Component | O-59724 | 7 | Steel Plate |  | 4 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 8 | Hex Head Screw M8x16 Cl 8.8 ZP |  | 128 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 9 | Nord-Lock Washer NL8 ZP |  | 128 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 10 | Hex Head Screw M10x25 Cl 8.8 ZP |  | 112 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 11 | Nord-Lock Washer NL10 ZP |  | 56 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 12 | Nord-Lock Washer NL10 ZP |  | 56 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 13 | Hex Head Screw M24x60 Cl 8.8 ZP |  | 8 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 14 | Nord-Lock Washer NL24 ZP |  | 8 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 15 | Hex Head Screw M30x80 Cl 8.8 ZP |  | 16 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 16 | Nord-Lock Washer NL30 ZP |  | 16 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Frame Machined | Fastener | O-59724 | 17 | Parallel Pin Ø30x80 |  | 8 | [8 empty] | WL-1-ALT-STR-FRM | 0
Stator Final Assembly | Component | O-59730 | 1 | Sole Plate - Stator Frame | Part drawing O-60066 (300865103) | 4 | [8 empty] | WL-1-ALT-STR | 0
Stator Final Assembly | Component | O-59730 | 2 | Wedge Pair | Wedge Pair 25x25x350 | 8 | [8 empty] | WL-1-ALT-STR | 0
Stator Final Assembly | Fastener | O-59730 | 3 | Hex Head Screw M30x110 Cl 8.8 | Hex Head Screw M30x110 Cl 8.8, ZP | 8 | [8 empty] | WL-1-ALT-STR | 0
Stator Final Assembly | Fastener | O-59730 | 4 | Washer to suit M30 | SHB 30 DIN7349 200 HV ST 2AC | 8 | [8 empty] | WL-1-ALT-STR | 0
Stator Final Assembly | Fastener | O-59730 | 5 | Parallel Pin | Ø30mm x 70mm | 16 | [8 empty] | WL-1-ALT-STR | 0
Stator Final Assembly | Fastener | O-59730 | 6 | Socket Head Cap Screw M30x70 Cl 8.8 | Socket Head Cap Screw M30x70 Cl 8.8, ZP | 8 | [8 empty] | WL-1-ALT-STR | 0
Stator Final Assembly | Fastener | O-59730 | 7 | Lock Washer | For Item 6, Nord-Lock NL30 ZP | 8 | [8 empty] | WL-1-ALT-STR | 0
Stator Core | Component | O-59723 | 1 | Stator Frame Machined | Refer O-59725 for entire assembly | 1 | [8 empty] | WL-1-ALT-STR-COR | 0
Stator Core | Component | O-59723 | 2 | Stator Sheets |  | 1 | [8 empty] | WL-1-ALT-STR-COR | 0
Stator Core | Component | O-59723 | 3 | Stator Core Iron RTD Sheet |  | 1 | [8 empty] | WL-1-ALT-STR-COR | 0
Stator Core | Component | O-59723 | 4 | Ventilation Sheet |  | 1 | [8 empty] | WL-1-ALT-STR-COR | 0
Stator Core | Component | O-59723 | 5 | Pressing Plate DE |  | 1 | [8 empty] | WL-1-ALT-STR-COR | 0
Stator Core | Component | O-59723 | 6 | Pressing Plate NDE |  | 1 | [8 empty] | WL-1-ALT-STR-COR | 0
Stator Core | Fastener | O-59723 | 7 | Stator Pressing Bolt | Bolt M20x1, 5x1158 | 41 | [8 empty] | WL-1-ALT-STR-COR | 1 (TBC)
Stator Core | Component | O-59723 | 8 | Adhesive Loctite 401 |  | 2 | [8 empty] | WL-1-ALT-STR-COR
Stator Core | Component | O-59723 | 9 | Dovetail Bar |  | 20 | [8 empty] | WL-1-ALT-STR-COR
Stator Core | Component | O-59723 | 10 | Compensation Sheets (Shims) for Dovetail Bar |  | 20 | [8 empty] | WL-1-ALT-STR-COR
Stator Core | Component | O-59723 | 11 | Covers (Pressing Plates) |  | 1 | [8 empty] | WL-1-ALT-STR-COR
Stator Core | Component | O-59723 | 12 | Band Steel | Used to tag along during stacking in order to maintain a back clearance of 0.25mm | N/A | [8 empty] | WL-1-ALT-STR-COR
Stator Winding | Component | O-59722 | 2 | Roebel Bar Bent (Top Bar) | Part drawing O-59916 (300865129) | 150 | [8 empty] | WL-1-ALT-STR-WDG | 16 (TBC)
Stator Winding | Component | O-59722 | 3 | Roebel Bar Bent (Bottom Bar) | Part drawing O-60191 (300865137) | 180 | [8 empty] | WL-1-ALT-STR-WDG | 2 (TBC)
Stator Winding | Component | O-59722 | 4 | Roebel Bar Bent (Connection Bar) | Part drawing O-60184 (30086540) | 30 | [8 empty] | WL-1-ALT-STR-WDG | 4 (TBC)
Stator Winding | Component | O-59722 | 5 | Seperator | 6x21x990 | 180 | [8 empty] | WL-1-ALT-STR-WDG | 20 (TBC)
Stator Winding | Component | O-59722 | 6 | Insulating Cap |  | 390 | [8 empty] | WL-1-ALT-STR-WDG | 40 (TBC)
Stator Winding | Component | O-59722 | 7 | Bracket for Winding Head DE |  | 15 | [8 empty] | WL-1-ALT-STR-WDG | 0
Stator Winding | Component | O-59722 | 8 | Bracket for Winding Head NDE |  | 15 | [8 empty] | WL-1-ALT-STR-WDG | 0
Stator Winding | Component | O-59722 | 9 | Support Ring Segments |  | 6 | [8 empty] | WL-1-ALT-STR-WDG | 0
Stator Winding | Component | O-59722 | 10 | Support Ring Segments |  | 6 | [8 empty] | WL-1-ALT-STR-WDG | 0
Stator Winding | Component | O-59722 | 11 | Support Ring Segments |  | 6 | [8 empty] | WL-1-ALT-STR-WDG | 0
Stator Winding | Component | O-59722 | 12 | Support Ring Segments |  | 6 | [8 empty] | WL-1-ALT-STR-WDG | 0
Stator Winding | Component | O-59722 | 13 | Stator Winding Connection Copper Parts Insulated | FLAT BAR 50 X 8 X 130 | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [6 empty] | WL-1-ALT-STR-WDG | 160 (TBC)
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 9 x 30 x 47 EPGC 203 - EN 60893 | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [6 empty] | WL-1-ALT-STR-WDG | 40 (TBC)
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 2 x 30 x 47 EPGC 203 - EN 60893 | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [6 empty] | WL-1-ALT-STR-WDG | 40 (TBC)
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 1 x 30 x 47 EPGC 203 - EN 60893 | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [6 empty] | WL-1-ALT-STR-WDG | 40 (TBC)
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 9 x 30 x 44 EPGC 203 - EN 60893 | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [6 empty] | WL-1-ALT-STR-WDG | 200 (TBC)
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 2 x 30 x 44 EPGC 203 - EN 60893 | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [6 empty] | WL-1-ALT-STR-WDG | 200 (TBC)
Stator Winding | Component | O-59722 | 60 | Stator Winding Connection Insul. Parts | 1 x 30 x 44 EPGC 203 - EN 60893 | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [6 empty] | WL-1-ALT-STR-WDG | 200 (TBC)
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 42mm | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [7 empty] | 140 (TBC)
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 47mm | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [7 empty] | 120 (TBC)
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 52mm | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [7 empty] | 120 (TBC)
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 37mm | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [7 empty] | 20 (TBC)
Stator Winding | Component | O-59722 | 71 | Slot Wedges | Slot Wedges 37mm | ? |  | Details come from Andritz spare parts FM-02285, detailed drawings listed are not with HT and limited info on O-59722 | [7 empty] | 20 (TBC)
Stator Winding |  | O-59722 | MORE
Air-Water Cooler |  | O-59797
Air Shield NDE Assembly |  | O-60169
Air Shield DE Assembly |  | O-60233

## Rotor
Project Number |  | H-0190022 |  |  | Site Manager | Josh Wilkes |  |  | Project Director |  |  | Jeremy Ramsey
Project Title |  | Wilmot Refurbishment |  |  | Project Manager | David Van Emmerik |  |  | Date |  |  | 2018-08-01
Details |  |  |  |  | Part Details |  |  |  | Ordering Information | [5 empty] | SAP & Spare Parts Information
Area | Part Type | Drawing Number | Part Number | Part | Description | Quantity | General Information | Comments | Details Confirmed | Supplied By | Who to Confirm | Ordered | Received | Location Stored | FLOC | Qty Spare | Material Number
Rotor Assembly | Component | O-27636 | 1 | Balancing weight | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 2 | Thrust Block Runner | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 3 | Fan Ring NDE | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 4 | Fan Ring DE | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 5 | Connection for Sliprings | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 6 | Damper Winding | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 7 | Field Winding | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 8 | Rotor Pole Complete | Detailed Drawing O-59714 | 10 | [8 empty] | WL-1-ALT-ROT-POL | 1
Rotor Assembly | Component | O-27636 | 9 | Sliprings | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 10 | Thrust Ring | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 11 | Thrust Ring | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 12 | Rotor Rim Punching | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 13 | Rotor Shaft | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 14 | Inner Oil Pot Cover | [10 empty] | WL-1-ALT-ROT | 0
Rotor Assembly | Component | O-27636 | 15 | Labyrinth Gland | [10 empty] | WL-1-ALT-ROT | 0
Rotor Pole Fixing | Component | O-59717 | 1 | Slide Wedge right | O-59928 (300889892) Pos 1 | 20 | [8 empty] | WL-1-ALT-ROT-POL | 2 (TBC)
Rotor Pole Fixing | Component | O-59717 | 2 | Slide Wedge left | O-59928 (300889892) Pos 2 | 20 | [8 empty] | WL-1-ALT-ROT-POL | 2 (TBC)
Rotor Pole Fixing | Component | O-59717 | 3 | Body Wedge right | O-59928 (300889892) Pos 3 | 20 | [8 empty] | WL-1-ALT-ROT-POL | 2 (TBC)
Rotor Pole Fixing | Component | O-59717 | 4 | Body Wedge left | O-59928 (300889892) Pos 4 | 20 | [8 empty] | WL-1-ALT-ROT-POL | 2 (TBC)
Rotor Pole Fixing | Fastener | O-59717 | 5 | Hex Head Screw M16x40 Cl 8.8 ZP |  | 40 | [8 empty] | WL-1-ALT-ROT-POL | 0
Rotor Pole Fixing | Fastener | O-59717 | 6 | Tab Washer 13mm | Tab Washer DIN93 13 ZP | 40 | For item 11 | [7 empty] | WL-1-ALT-ROT-POL | 0
Rotor Pole Fixing | Component | O-59717 | 7 | Stop Block |  | 40 | [8 empty] | WL-1-ALT-ROT-POL | 0
Rotor Pole Fixing | Component | O-59717 | 8 | Stop Angle |  | 40 | [8 empty] | WL-1-ALT-ROT-POL | 0
Rotor Pole Fixing | Fastener | O-59717 | 9 | Hex Head Screw M10x20 Cl 8.8 ZP |  | 80 | [8 empty] | WL-1-ALT-ROT-POL | 0
Rotor Pole Fixing | Fastener | O-59717 | 10 | Tab Washer 10.5mm | Tab Washer DIN93 10.5 ZP | 80 | [8 empty] | WL-1-ALT-ROT-POL | 0
Rotor Pole Fixing | Fastener | O-59717 | 11 | Hex Head Screw M12x30 Cl 8.8 ZP |  | 40 | [8 empty] | WL-1-ALT-ROT-POL | 0
Rotor Pole Fixing | Component | O-59717 | 12 | Compensating sheet for pole fixing (Shim) |  | 10 | [8 empty] | WL-1-ALT-ROT-POL | TBC
Rotor Pole Fixing | Fastener | O-59717 | 20 | Tab Washer 17mm | Tab Washer DIN93 17 ZP | 40 | [8 empty] | WL-1-ALT-ROT-POL | 0
Rotor Pole Fixing | Component | O-59717 | 21 | Stop Block |  | 40 | [8 empty] | WL-1-ALT-ROT-POL | 0
Rotor Pole Damper Connection |  | O-59719- | 1 | DAMPER CONNECTION LINK | -DRW300865192- | 4
Rotor Pole Damper Connection |  | O-59719- | 2 | DOVETAIL PIECE LONG | DWG.NO. 300865193 POS. 2 | 1
Rotor Pole Damper Connection |  | O-59719- | 3 | TENSION BOLT DAMPER CONNECTION | -DRW300865194- | 2
Rotor Pole Damper Connection |  | O-59719- | 4 | THREAD PLATE W. CHAMFER M10 |  | 4
Rotor Pole Damper Connection |  | O-59719- | 5 | Hex Head Screw M10x40 Cl 8.8 ZP |  | 8
Rotor Pole Damper Connection |  | O-59719- | 6 | SPRING WASHER DIN6796 |  | 8
Rotor Pole Damper Connection |  | O-59719- | 7 | TWO-HOLE LOCK PLATE 10,5X 33 |  | 4
Rotor Pole Damper Connection |  | O-59719- | 8 | HEX NUT ISO4032 Cl 8.8 M20 ZP |  | 2
Rotor Pole Damper Connection |  | O-59719- | 9 | Tab Washer 21mm | Tab Washer DIN93 21mm ZP | 2
Rotor Pole Damper Connection |  | O-59719- | 10 | Hex Head Screw M12x60 Cl 8.8 ZP |  | 2
Rotor Pole Damper Connection |  | O-59719- | 11 | HEX NUT ISO4032 Cl 8.8 M12 ZP |  | 2
Rotor Pole Damper Connection |  | O-59719- | 12 | Tab Washer 13mm | Tab Washer DIN93 13mm ZP | 2
Rotor Pole Damper Connection |  | O-59719- | 13 | DOVETAIL PIECE SHORT | DWG.NO. 300865193 POS. 13 | 1
Rotor Pole Connection | Component | O-59718 | 1 | POLE CONNECTION, COPPER PARTS | -DRW300865190- | 1
Rotor Pole Connection | Component | O-59718 | 2 | TENSION BOLT | SEE DWG.NO. 300865189 POS. 2 | 9
Rotor Pole Connection | Component | O-59718 | 3 | PRESSURE PLATE | SEE DWG.NO. 300865189 POS. 3 | 18
Rotor Pole Connection | Component | O-59718 | 4 | INSULATING PART | SEE DWG.NO. 300865188 POS. 4 | 18
Rotor Pole Connection | Component | O-59718 | 5 | INSULATING TUBE | SEE DWG.NO. 300865188 POS. 5 | 9
Rotor Pole Connection | Component | O-59718 | 6 | THREAD PLATE W. CHAMFER | M 8 X=25 S690QL-DRW3461935 | 36
Rotor Pole Connection | Fastener | O-59718 | 7 | HEX HEAD SCREW ISO4017 - M8X20 -Cl8.8 ZP |  | 72
Rotor Pole Connection | Fastener | O-59718 | 8 | TWO-HOLE LOCK PLATE | 8,4X 25 | 36
Rotor Pole Connection | Fastener | O-59718 | 9 | SPRING WASHER | DIN6796 - 8 - SPRING STEEL | 72
Rotor Pole Connection | Fastener | O-59718 | 10 | HEX NUT M20 Cl8 ZP |  | 18
Rotor Pole Connection | Fastener | O-59718 | 11 | Tab Washer 21mm | Tab Washer DIN93 21mm ZP | 18

## FLOC
Functional loc. | WL
Description | Wilmot
WL
WL-1 | No.1 Machine
WL-1-ALT | Alternator
WL-1-ALT-BJA | Brakes & Jacks Assembly
WL-1-ALT-FDS | Alternator Fire Suppression System
WL-1-ALT-GB1 | Lower Guide Bearing
WL-1-ALT-GB1-HTX | Guide Bearing Heat Exchanger
WL-1-ALT-HTX | Alternator Air Coolers (4 of)
WL-1-ALT-PMG | PMG
WL-1-ALT-ROT | Rotor
WL-1-ALT-ROT-POL | Rotor Poles
WL-1-ALT-SHT | Alternator Shaft
WL-1-ALT-STR | Stator
WL-1-ALT-STR-COR | Stator Core
WL-1-ALT-STR-FRM | Stator Frame
WL-1-ALT-STR-WDG | Stator Winding
WL-1-ALT-THG | Combination Thrust / Guide Bearing
WL-1-ALT-THG-GB1 | Thrust/Guide Bearing - Guide Bearing
WL-1-ALT-THG-HTX | Thrust/Guide Bearing Heat Exchangers
WL-1-ALT-THG-HTX-001 | Thrust/Guide Bearing Heat Exchanger No.1
WL-1-ALT-THG-HTX-002 | Thrust/Guide Bearing Heat Exchanger No.2
WL-1-ALT-THG-THR | Thrust/Guide Bearing - Thrust Bearing
WL-1-BUS | 11 kV Busbar
WL-1-CWS | Cooling Water System
WL-1-CWS-FLR | Cooling Water Flow Relays
WL-1-CWS-FLR | Cooling Water Filter System
WL-1-CWS-PS1 | Cooling Water Pumpset No.1
WL-1-CWS-PS2 | Cooling Water Pumpset No.2
WL-1-CWS-PS3 | Chemical Injection Pumpset
WL-1-EXS | Excitation System
WL-1-EXS-AVR | Auto Voltage Regulator
WL-1-EXS-BGR | Brushgear & Slip Rings
WL-1-EXS-FSW | Field Switch
WL-1-GOV | Governor
WL-1-GOV-CTE | Governor Control
WL-1-GOV-HYD | Governor Hydraulic System
WL-1-GOV-HYD-FLT | Governor Oil Filter System
WL-1-GOV-HYD-PS1 | Governor Pumpset No.1
WL-1-GOV-HYD-PS1-SV1 | Hydraulic Pressure Relief Valve
WL-1-GOV-HYD-PS1-ULA | Unloader Valve
WL-1-GOV-HYD-PS2 | Governor Pumpset No.2
WL-1-GOV-HYD-PS2-SV1 | Hydraulic Pressure Relief Valve
WL-1-GOV-HYD-PS2-ULA | Unloader Valve
WL-1-GOV-HYD-PV1 | Governor Air-Oil Accumulator
WL-1-GOV-HYD-PV1-PG1 | Pressure Gauge
WL-1-GOV-HYD-PV1-SV1 | Pressure Relief Valve, Accumulator Air
WL-1-HTV | Hilltop Valve
WL-1-HTV-ACS | HTV AC Supplies
WL-1-HTV-ACS-TFR | HTV Services Transformer
WL-1-HTV-CTE | HTV Control Equipment
WL-1-HTV-DCS | HTV DC Supplies
WL-1-HTV-DCS-BY1 | HTV 48V Battery
WL-1-HTV-DCS-CH1 | HTV 48V Battery Charger
WL-1-HTV-HYD | HTV Hydraulic System
WL-1-HTV-HYD-PS1 | Hydraulic Pumpset No.1
WL-1-HTV-HYD-PS2 | Hydraulic Pumpset No.2
WL-1-MCW | Machine Control Water System
WL-1-MCW-FLT | Machine Control Water Filter System
WL-1-MIV | Main Inlet Valve
WL-1-MIV-ACT | MIV Actuators
WL-1-MIV-BV1 | MIV Bypass Valve Assembly
WL-1-MIV-CTE | MIV Control Equipment
WL-1-MPC | Machine Protection & Controls
WL-1-MPC-EPS | Generator Protection
WL-1-MPC-MPS | Mechanical Protection
WL-1-MPC-SYN | Synchronizer
WL-1-MPC-UCA | Unit Control
WL-1-NT1 | Wilmot Intake
WL-1-NT1-ACS | Intake AC Supplies
WL-1-NT1-ACS-TFR | Intake Services Transformer
WL-1-NT1-ACT | Intake Actuator
WL-1-NT1-BR1 | Wilmot Intake Tower Bridge
WL-1-NT1-CHM | Intake Cranes, Hoists, Monorails
WL-1-NT1-CHM-CR1 | Intake Stop Log Hoist & Gantry (8T)
WL-1-NT1-CHM-CR1-RG1 | Trash Rack Rake
WL-1-NT1-CHM-CR1-RG1-GW1 | Trash Rack Rake Winch Unit
WL-1-NT1-DCS | Intake DC Supplies
WL-1-NT1-DCS-BY1 | Intake Battery 48V
WL-1-NT1-DCS-CH1 | Intake 48V Battery Charger
WL-1-NT1-GT1 | Intake Gate Assembly
WL-1-NT1-GT1-CTE | Intake Gate Control Equipment
WL-1-NT1-HYD | Intake Hydraulic system
WL-1-NT1-HYD-PS1 | Intake Hydraulic Pumpset
WL-1-NT1-TRK | Trash Rack
WL-1-PP1 | Wilmot Penstock
WL-1-PP1-OV1 | Over-Velocity Device
WL-1-PP1-V01 | Neyrpic Valve 1 Upstream of HTV.
WL-1-PP1-V02 | Neyrpic Valve 2 Downstream of HTV.
WL-1-PP1-V03 | Neyrpic Valve 3 Downstream of HTV.
WL-1-PP1-V04 | Anti-Vac Valve No.1
WL-1-PP1-V05 | Anti-Vac Valve No.2
WL-1-PP1-V06 | Air Valve
WL-1-RVV | Turbine Relief Valve
WL-1-RVV-DTU | Relief Valve Draft Tube
WL-1-RVV-SLG | Relief Valve Stoplogs
WL-1-SGR | Machine Switchgear
WL-1-SGR-X01 | Circuit Breaker 52
WL-1-SGR-Y01 | Isolator 29 & Earthswitch 31
WL-1-TFR | Machine Transformers & Reactors
WL-1-TFR-DV1 | Surge Diverter
WL-1-TFR-ET1 | Excitation Transformer
WL-1-TFR-ITF | Machine Instrument Transformers
WL-1-TFR-ITF-001 | Current Transformers 96 (A,B,C)
WL-1-TFR-ITF-002 | Current Transformers 96 (D, E, F)
WL-1-TFR-ITF-003 | Voltage Transformer 97A
WL-1-TFR-ITF-004 | Voltage Transformer 97B
WL-1-TFR-ITF-005 | Voltage Transformer 97C
WL-1-TFR-ITF-006 | Air Gap Reactor (90m322)
WL-1-TFR-PT1 | Power Transformer
WL-1-TFR-PT1-BSH | Transformer Bushings
WL-1-TFR-PT1-HTX | Transformer Heat Exchangers
WL-1-TFR-PT1-HTX-001 | Transformer Heat Exchanger No.1
WL-1-TFR-PT1-HTX-002 | Transformer Heat Exchanger No.2
WL-1-TFR-PT1-PRT | Transformer Protection
WL-1-TFR-PT1-PS1 | Transformer Oil Pumpset No.1
WL-1-TFR-PT1-PS2 | Transformer Oil Pumpset No.2
WL-1-TFR-UT1 | Unit Transformer
WL-1-TUR | Turbine
WL-1-TUR-AAS | Air Admission System
WL-1-TUR-COV | Top / Bottom Cover Assembly
WL-1-TUR-DTU | Draft Tube
WL-1-TUR-DTU-CD1 | Draft Tube Conduit
WL-1-TUR-DTU-CNE | Draft Tube Cone
WL-1-TUR-GB1 | Turbine Bearing
WL-1-TUR-GB1-HTX | Turbine Bearing Heat Exchanger
WL-1-TUR-GVA | Guide Vane Assemblies
WL-1-TUR-GVA-001 | Guide Vane No.01
WL-1-TUR-GVA-002 | Guide Vane No.02
WL-1-TUR-GVA-003 | Guide Vane No.03
WL-1-TUR-GVA-004 | Guide Vane No.04
WL-1-TUR-GVA-005 | Guide Vane No.05
WL-1-TUR-GVA-006 | Guide Vane No.06
WL-1-TUR-GVA-007 | Guide Vane No.07
WL-1-TUR-GVA-008 | Guide Vane No.08
WL-1-TUR-GVA-009 | Guide Vane No.09
WL-1-TUR-GVA-010 | Guide Vane No.10
WL-1-TUR-GVA-011 | Guide Vane No.11
WL-1-TUR-GVA-012 | Guide Vane No.12
WL-1-TUR-GVA-013 | Guide Vane No.13
WL-1-TUR-GVA-014 | Guide Vane No.14
WL-1-TUR-GVA-015 | Guide Vane No.15
WL-1-TUR-GVA-016 | Guide Vane No.16
WL-1-TUR-GVA-017 | Guide Vane No.17
WL-1-TUR-GVA-018 | Guide Vane No.18
WL-1-TUR-GVA-019 | Guide Vane No.19
WL-1-TUR-GVA-020 | Guide Vane No.20
WL-1-TUR-RGS | Reg Ring & Servomotor Assembly
WL-1-TUR-RGS-ACT | Servomotor
WL-1-TUR-RUN | Runner Assembly
WL-1-TUR-SHT | Turbine Shaft
WL-1-TUR-SHT-SEA | Turbine Shaft Seal
WL-1-TUR-SLG | Draft Tube Stoplogs
WL-1-TUR-SPR | Spiral Casing
WL-C | Civil & Dams
WL-C-AWW | Access and Walkways
WL-C-DAM | Dams & Catchments
WL-C-DAM-D01 | Wilmot Dam
WL-C-DAM-D01-CD1 | Wilmot Riparian Outlet
WL-C-DAM-D01-CD1-V01 | Wilmot Riparian Valve
WL-C-DAM-D01-CD1-V02 | Wilmot Riparian Guard Valve
WL-C-DAM-D01-CD2 | Wilmot Dam Dewatering System
WL-C-DAM-D01-CD2-CPN | Cathodic Protection
WL-C-DAM-D01-CD2-DOM | Dewatering Dome
WL-C-DAM-D01-MON | Wilmot Dam Monitoring System
WL-C-DAM-D01-MON-001 | Wilmot V-Notch No.1 (Dam)
WL-C-DAM-D01-MON-002 | Wilmot Left Hand Side V-Notch in Tunnel
WL-C-DAM-D01-MON-003 | Wilmot Right Hand Side V-Notch in Tunnel
WL-C-DAM-D01-SPY | Wilmot Spillway
WL-C-DAM-D01-TUN | Wilmot Diversion Tunnel
WL-C-DAM-S01 | Lake Gairdner
WL-C-DAM-S01-RP1 | Boat Ramp
WL-C-RMN | Remote Monitoring Sites
WL-C-RMN-001 | Iris River - At Middlesex Plains
WL-C-RMN-002 | Gairdner Lake - At Intake
WL-C-RMN-003 | Iris River - Pluvio
WL-C-RMN-004 | Gairdner Lake - Pluvio
WL-C-TRC | Wilmot Tailrace
WL-C-TUN | Wilmot Tunnels
WL-C-TUN-001 | Wilmot Headrace Access Adit
WL-C-TUN-002 | Wilmot Headrace Tunnel
WL-E | Earthing
WL-E-E01 | Station Earthing
WL-E-E02 | Switchyard Earthing
WL-E-E03 | Penstock Earthing
WL-E-E04 | Headworks Earthing
WL-E-TEQ | Earthing Tools & Equipment
WL-F | Land & Facilities
WL-F-BLD | Wilmot Buildings
WL-F-BLD-001 | Wilmot Power Station
WL-F-BLD-001-SEW | Sewerage System
WL-F-BLD-001-STW | Stormwater Drainage System
WL-F-BLD-001-WAT | Domestic Water System
WL-F-BLD-002 | Wilmot Intake Building
WL-F-BLD-003 | Wilmot HTV House
WL-F-BLD-004 | Wilmot Gate Flammable Store
WL-F-BLD-005 | Wilmot Neypric House
WL-F-EAS | Wilmot Easements
WL-F-EAS-001 | tnlE- over Wilmot Headrace Tunnel
WL-F-EAS-002 | Wilmot Wayleave Easements
WL-F-EAS-002-001 | wylvE 1 - Power Line (Lake Gairdner)
WL-F-EAS-002-002 | wylvE 2 - Power Line (Lake Gairdner)
WL-F-LND | Wilmot Land
WL-F-LND-001 | Power Station Land
WL-F-LND-002 | Switchyard Compound
WL-F-LND-002-BND | Switchyard Compound Oil Bunding
WL-F-LND-003-001 | Lake Gairdner Land 1
WL-F-LND-003-002 | Lake Gairdner Land 2
WL-F-LND-003-003 | Lake Gairdner Land 3
WL-F-LND-003-004 | Lake Gairdner Land 4
WL-F-LND-003-005 | Lake Gairdner Land 5
WL-F-LND-003-006 | Lake Gairdner Land 6
WL-F-LND-003-007 | Lake Gairdner Land 7
WL-F-LND-003-008 | Lake Gairdner Land 8
WL-F-LND-003-009 | Lake Gairdner Land 9
WL-F-LND-004 | Wilmot Dam Land - Lake Gairdner
WL-R | Wilmot Roads
WL-R-R01 | Wilmot Power Station Road
WL-R-R02 | Wilmot Hilltop Valve Road
WL-R-R03 | Wilmot Dam Access Road
WL-S | Station Services
WL-S-ACS | Station AC Supplies
WL-S-ACS-EG1 | 100 kvA Generator Set
WL-S-ACS-TFR | Station Services Transformer
WL-S-CAS | Compressed Air System
WL-S-CAS-CP1 | Governor Air Compressor
WL-S-CAS-CP1-SV1 | Pressure Relief Valve, Interstage
WL-S-CAS-CP1-SV2 | Pressure Relief Valve, Compressor
WL-S-CAS-CP2 | Portable Air Compressor
WL-S-CAS-CP2-PV1 | Portable Air Compressor Air Receiver
WL-S-CAS-CP2-PV1-PG1 | Pressure Gauge
WL-S-CAS-CP2-PV1-SV1 | Pressure Relief Valve
WL-S-CHM | Cranes, Hoists, Monorails
WL-S-CHM-CR1 | Station Crane
WL-S-CHM-CR2 | Draft Tube Stoplog Gantry Crane (5T)
WL-S-CHM-HT1 | Control Water Filter Hoist (1T)
WL-S-CHM-HT2 | Control Filters Davit Arm
WL-S-CHM-MR1 | Dewatering Pit Monorail (250Kg)
WL-S-CHM-MR2 | Neyrpic Valve House Monorail (1T)
WL-S-DCS | DC Supplies
WL-S-DCS-BY1 | Station A Battery 125V
WL-S-DCS-BY2 | Station B Battery 125V
WL-S-DCS-CH1 | Battery Charger 125V "A"
WL-S-DCS-CH2 | Battery Charger 125V "B"
WL-S-DCS-CNV | DC Converters
WL-S-DW1 | Dewatering System
WL-S-DW1-PS1 | Dewatering Pumpset No.1
WL-S-DW1-PS2 | Dewatering Pumpset No.2
WL-S-DW1-PS3 | Dewatering Emergency Pump
WL-S-DW1-SK1 | Dewatering Pit Oil Skimmer
WL-S-FCW | Fire Control & Water Supplies
WL-S-FCW-FDS | Fire Detection System
WL-S-FCW-FDS-PN1 | Main Fire Panel
WL-S-FCW-PWV | Fire Hydrants & Pipework
WL-S-FCW-TNK | Reservoirs (2 Tanks)
WL-S-FCW-TNK-001 | Firewater Tank No.1
WL-S-FCW-TNK-002 | Firewater Tank No.2
WL-S-SEC | Security & Access System
WL-S-SPC | Station Protection & Control
WL-S-SPC-FLP | Flood Protection System
WL-S-SPC-RTU | RTU
WL-S-SPC-TLP | Transmission Line Protection
WL-S-TEQ | Tools & Equipment
WL-S-TEQ-LFT | Lifting Equipment
WL-S-TEQ-OHE | Oil Handling Equipment
WL-S-TEQ-PLD | Portable Ladders
WL-S-TEQ-SEQ | Safety Equipment
WL-S-TEQ-WP1 | Inspection Platform
WL-S-TEQ-WST | Workshop Tooling
WL-Y | Telecommunications
WL-Y-RLK-001 | Wilmot Power Station Cethana Dam Comms
WL-Y-RLK-002 | Wilmot HTV Cethana Dam Comms Site